### CONTENTS

1.0 Alarm Relay

1.1    Operation

1.2    Wiring

1.3    Install - Verify

1.0 Alarm Relay

1.1 Operation

The Alarm Relay dry contact set changes state when:

- Any controller sensor, meter, contact set, pump, valve or system alarm occurs.

- When the controller loses AC power.

The Alarm relay has both NC (Normally Closed) & NO (Normally Open) dry contacts.

When an Alarm occurs the to NC-to-COM circuit opens and the NO-to-COM circuit closes.

The Alarm dry contacts are rated 250mA @ 250VAC, 500mA @ 125VAC and 2Amps at 30VDC.

1.2 Wiring

The Alarm relay wiring block is rated for AWG 14-26, 300V & 10A

Most alarms to monitoring DCS (Distributed Control Systems) will be wired AWG18-22.

Best practice is to wire the alarm to the NC & COM contact set which will open on Alarm.

Loss of controller AC power, a cable break-disconnect and an actual controller alarm will all result in an alarm.

1.3 Install Verify

1.3.1 Install

Parts required:

- Aegis_AD alarm relay card

- 12”to18” ribbon cable with socket connectors (Digikey H3AAH-1018-ND or equivalent)

- Two #6-26 ‘Nylok’ hex nuts

Verify that the upper, Measure Aegis circuit board has an installed 10 pin ribbon cable ‘Modem’ socket above the LCD display (Digikey A33159-ND or equivalent).

Install sequence:

- Unplug controller AC power & remove the clear AC shield.

- Connect the flat cable to the Aegis_AD card ensuring the RED side of the cable aligns with the RED 1 text on the Aegis_AD card.

- Place the Aegis_AD on the 3 existing backplate studs under the power circuit board.

- Plug the other end of the ribbon cable into the measure circuit board Modem socket with RED side to the left.

- Install 6-32 hex ‘Nylok’ nuts on the front two Aegis_AD mounting screws.

- Replace the AC shield & plug in the controller AC power.

Note:

Because the Aegis_AD uses the controller Modem connector, the modem and alarm relay controller options are mutually exclusive.

1.3.2 Verify - Browser

Browse the controller at any password level and select

System /  Diagnostic.

Alarm Relay will be Yes if the controller locates the Aegis_AD card at power ON.

The Alarm Relay line of the Diagnostic page exists in firmware Versions A889 & M889 (Modbus option) from 08/09.

1.3.2 Verify - Keypad

| Key ENTER @ power ON screen. Or Key EXIT until you get to this screen Key ENTER @ Diagnostic. Key UP @ Relay Fuse. Alarm Relay will display Yes if the controller has detected the Aegis_AD card on power up or No if the card is not installed. |  |  |
| --- | --- | --- |