SMART ‘AS’ Automated Service

Water Management Controllers

Cooling Tower, Waste Water & Process

INSTALLATION & MAINTENANCE

MANUAL

Version 4.09 Controller Software

8660 Red Oak ( Rancho Cucamonga ( California  (  91730

contents 1 of 2

1. READ-ME!																1

1.1  Check controller box contents								1

1.2  Where’s the information for this controller?	     			1											1.3  Where can I get more information?							1

2. INSTALLATION

2.1  Enclosure Installation											2

2.2  Sample Piping and Sensor Installation						3

2.3  Cabling Sensors, Pumps, Valves, Solenoids, Meters   	5

2.4  Terminal Block Locations										6

2.5  Connecting pH or ORP Sensors								7

2.6  Connecting Conductivity-Temperature Sensors			7

2.7  Connecting Watermeters										8

2.8  Connecting 4-20mA Sensors & Liquid Level Sensors 	10

2.9  Connecting Flowswitches and Level Switches			11

2.10 Connecting AC Power, Solenoids & Pumps				12

2.11 Connecting Alarms and Motorized Valves				13

2.12 Connecting Serial Cables, Telephone Modem or		14

Controller Network

3. COMMISSIONING

3.1 Set-up Controller													15

3.2 Quik Operate 														17

3.2.1	View what happening now							17

3.2.2	Adjust a Setpoint										18

3.2.3 	View what’s causing an alarm						19

3.2.4 	Calibrate a Sensor									19

4. CONFIGURING

4.1   CONTROLLER DISPLAY										21

4.2   ‘TV’ REMOTE KEYS & PROGRAMMING					22

4.3	   MAIN MENU OPTIONS											24

4.4   ADJUST SETPOINTS 											26

4.5   ADJUST BIOTIMING											27

4.6   VIEW ACTIVE ALARMS										29

4.7   CLEAR ALARMS												29

4.8   ADJUST ALARMS												30

4.9   ADJUST DATE & TIME											31

4.10 CALIBRATE SENSORS										31

4.11 VIEW WATERMETERS											35

4.12 PRIME PUMPS													35

4.13 BIOCIDE LOCKOUT											36

4.14 INHIBITOR CONTROL											37

4.15 ADJUST 4-20mA LOOPS										39

4.16 ADJ. ENABLED PARAMS										40

4.17 ADJ. SITE SETTINGS											41

contents 2 f 2

5. OPERATION & MAINTENANCE

5.1  ‘Out-of-the-Box’ Operation								43

5.2 Setpoint  Guidelines											44

5.2.1 Conductivity										44

5.2.2 pH/ORP											44

5.2.3 Inhibitor Control								44

5.3 Calibration														45

5.4 Biocide Timed Events										45

5.5 Alarms															45

5.6 Fault-Cause Summary										47

5.6.1  NO POWER-NO DISPLAY						47

5.6.2  NO CONDUCTIVITY CONTROL					47

5.6.3  NO pH or ORP CONTROL						48

5.6.4  NO BIOICDE FEED								48

5.6.5  NO TV REMOTE KEYPAD OPERATION		49

6. PRODUCT SUPPORT												49

APPENDIX ‘A’ CONTROLLER OPTIONS

& Sensor Part Numbers				50

APPENDIX ‘B’ TV Remote Keypad Menu Tree 		51

APPENDIX ‘C’ Options Sub-Panel			 				54

USER WARNING : CAUTION

Water Treatment Controllers operate steam and water valves and may pump hazardous, corrosive and toxic chemicals. Opening the controller enclosure exposes user to the risk of electrical shock at power line voltages.

Understand fully the implications of the control setpoints, interlocks and alarms that you select. Harm to personnel and damage to equipment may result from mis-application.

Unplug or turn OFF the AC power to the controller if you have any concerns regarding safety or incorrect controller operation and notify supervisory staff.

YOUR CONTROLLER

Aquatrac controllers are supplied in many different configurations.

The HELP section in the back of this manual contains the Field Wiring information for terminating the sensors supplied with your specific controller.

The HELP section in the back of this manual contains the installation plumbing header which shows the sensor set supplied with your specific controller.

1. READ ME!

1.1  Check controller box contents

Automated Service, ‘AS’ series controllers are shipped configured for many applications.

The sensor set required for your controller is shipped with a ¾” SCH80 PVC installation header.

If your controller includes pH, ORP or corrosion rate sensors, they are shipped in the controller box separately 	packaged in	their own boxes. Do not remove these sensors from their protective packaging until ready to turn 	on sample piping water and commission the controller.

All other sensors; conductivity, flowswitch(es) are shipped installed in the installation header.

If your controller is configured for multiple towers or processes, you may have more than one sensor header.

See HELP section at the back of this manual, for a drawing of the header shipped with your controller

Verify that your controller includes the required sensors, this operating manual and a TV remote keypad.

1.2  Where’s the information for this controller?

This is a generic manual for all of Smart ‘AS’ Tower, Closed Loop, Process and Waste Water applications.   Boilers are supported in a separate manual.

The Technical Manual for this controller is available at www.aquatrac.com

Detail for your controller and its sensor set is in the HELP section at the back of this manual

Identify the sensors and options purchased with your controller by the label located at the bottom, inside of the enclosure door below the controller circuit card.

You’ll see a part number that looks like this SAT CP T2 L2 R2 AD.

The first three letters identify a controller family and the following letters identify options.

Flip to Appendix ‘A’ & you’ll see what sensors and functions are included with your controller.

These letter 	codes are used throughout the Manual so you’ll know if the instructions apply to your controller.

1.3  Where can I get more information?

See Section 4. for an explanation of what you’re seeing as the	 display scrolls & the TV remote Keypad commands.  www.aquatrac.com has both operating and technical manuals.

The HELP section at the back of this manual has information specific to your specific controller Part# set-up and sensor set.

The Technical manual for ‘AS’ series controllers, available at www.aquatrac.com as

Flx-AS_TechMan.doc, contains advanced troubleshooting sequences and detail on communication and sensor specifications.

2. INSTALLATION

HELP: Wiring details and options unique to your controller are detailed in the 											HELP section at the back of this manual

2.1 Enclosure Installation

Wall mount controller enclosures so that the front panel display is at chest level, placing the top of the 	enclosure at 	nominally 5 ft. above the floor. Select a location:

1. To minimize sample piping distance.

2. Close to chemical drums.

3. Beside an electrical outlet.

4. With 12” of clear wall below and on both sides of the enclosure.

5. Which allows 180 degree door opening for left hand side hinged door.

| Controller Type | Mounting Hole Centers | Mounting Hole Size |
| --- | --- | --- |
| SAT…. | 10.75” V x 6” H | 4 x 5/16”D corner mount |
| SAT….RM | 12.75” V x 8” H | 4 x 5/16”D corner mount |
| Option LE16-14 | 16.75” V x 12” H | 4 x 5/16”D corner mount |

PUMP PLUG ENCLOSURES

The chemical pump plug enclosures are labeled with the chemical pump and bleed solenoid designations to 		match each controller’s options.

The pump plug enclosures may be disconnected from the controller and extended with EMT or rigid conduit.

Note the color coding before disconnecting the 120VAC power cabling and extend the cabling in AWG14 to 			AWG18 gauge cable, preserving the color original coding

2.2 Sample Piping and Sensor Installation

Plumb the sensor header across the recirculating pump or condenser pressure drop so that a minimum of		     1 GPM flows across the sensors and flow switch ( Controllers with an F 	option include a flow switch) 					sensors. The following graphic shows a typical sensor only installation.

Chemical injection manifold detail is shown on the following page.

Schedule 80, 3/4” solvent  weld  PVC is recommended for low pressure cooling tower sample piping.

CAUTION: High rise buildings and piping systems with pressures over 100 psi will require sensors, entry							 fittings and flowswitch(es) rated for the expected static head and operating pressure at the 								sensor location.

CAUTION: pH & ORP Sensor Installation

ORP and pH sensors should be installed vertically, with the measuring tip pointed down.

Horizontal sensors are more likely to fail due to air bubbles in the sensor tip.

2.3 Cabling Sensors, Pumps, Valves, Solenoids, Meters ...

CAUTION ELECTRICAL SHOCK HAZARD

Unplug the controller before opening the controller enclosure

and installing or changing any wiring or cabling

CABLING RULES

Sensor and AC power cables must be installed in separate conduits.

Mixing sensor, valve and pump cable in one conduit will cause intermittent controller operating problems, 	false and unstable conductivity and pH measurements and overstated water meter readings.

Extending Sensor, Flowswitch and Water Meter Cables

All sensor, watermeter and flowswitch extension cables are twisted pair AWG16 to AWG24, 							shielded cable with the shields terminated to the enclosure grounding screws at the bottom, left of the 				enclosure.  Shields are not grounded or terminated at the sensor end.

Extending Conductivity Sensor Cables

Conductivity sensor cables measuring conductivities greater than 5000uS may be extended up to 						200 ft using AWG22 gauge twisted pair, shielded cable.  Conductivities above 5000uS and below 						10,000uS require AWG18 gauge cable at 200 ft.

Extending pH Electrode Cables

pH electrode cables over 25ft long are susceptible to noise pickup from lights and motors which appears 			as 	an unstable pH display.  Battery powered pH sensors are recommended for longer cabling 							lengths and in electrically noisy locations.

Low impedance ORP electrodes can usually be cabled up to 200ft from the controller without 							using an amplified sensor.

120VAC CABLING

Do not connect AWG14 & heavier seven stranded cable directly to the controller door terminal blocks.

Controllers are fused for AWG18 allowing you to butt splice AWG12-14 field wiring to AWG 18-16	 					before connecting to the door terminal blocks.

CONNECTING 7 STRAND CABLE TO DOOR TERMINAL BLOCKS WILL BREAK THE  									TERMINAL  BLOCK OFF THE CIRCUIT BOARD

FRACTIONAL HORSEPOWER PUMPS

External motor starter rated relays are required for fractional horsepower Milton Roy or Neptune						chemical feed pumps. Connecting fractional horsepower pumps directly to the controller will fail the 					controller fuse and may fuse the power relay contacts closed.

The 120VAC coils of the starter relays, located in an external enclosure, are powered by the							AS series controller relays.

DO NOT power fractional horsepower pumps from the same AC circuit breaker that feed the controller.

#### ROUTING USER INSTALLED CABLING

User installed sensor cabling must be routed away from 120VAC cabling. The central set of

cabling clips on the ’AS’ backplate are provided for sensor, flow switch  and water meter cables.

Ensure that when the enclosure door opens and closes the sensor cable falls to the right hand side of 				the enclosure.

Use the left hand set of cable clips for AC power cables.

2.4 Terminal Block Locations

2.5 Connecting pH or ORP Sensors

Route the electrode cabling across the bottom of the terminal blocks, away from 120VAC pump, 						valve and solenoid cables. Coil extra sensor cable at the sensor, not in the controller 										enclosure.

Controllers with more than one pH or ORP sensor: Connect the extra sensor(s) to modules in the 		back of the controller enclosure – See Appendix C.

2.6 Connecting Conductivity-Temperature Sensors

Controllers with more than one conductivity sensor: Connect the extra sensor(s) to modules in the 						back of the controller enclosure – See Appendix C.

‘AS’ series controllers allow direct connection of a conductivity sensor to the controller.

Additional conductivity sensors require sensor driver boards either located on a sub-panel within the

enclosure or in an external enclosure.

NOTE:	Cooling Water conductivity sensors which directly connect to the controller use electronic 								temperature sensors for compensation  Part#  A261200.

Added conductivity sensors use thermistor compensation  Part A261003.

Direct Connect and Additional conductivity sensors are therefore NOT interchangeable.

2.7 Connecting Watermeters

Water meters require software configuration the set the gallons per contact or the ‘K’ factor for 						turbines and paddlewheels.

CONTACT HEAD WATER METERS WIRING

Cable the two conductor meter cables to any two of the terminals labeled

O+ & O-,  P+ & P- and  Q+ & Q-.

TURBINE & PADDLEWHEEL METER WIRING

Cable the three wire sensors to the any of the three connections labeled

P(12VDC Power), + (Signal) & 	-  (Common or Ground)

Color coding varies with manufacturer.

Aquatrac paddlewheel water meters connect Red to P, White to +  and Black to -.

The scaling factor printed on the side of the meter is Pulses per Gallon

Osmonics turbine meters connect Red to P, Black to +  and White to -.

WATER METER SOFTWARE CONFIGURATION.

TRACKSTER or the TV Remote keypad can be used to convert water meter signals into 								Gallons, liters, cubic feet .....

The TV Remote uses the CALIBRATION menu where SCALE and ‘K’ Factor are used.

| Meter | TV Remote Keypad | Trackster | ‘PA’ Command |
| --- | --- | --- | --- |
| Contact Head 100 Gallons/Contact Connected to ‘O’ | Parameter ‘O’ Scale = 0 ‘K’ Factor = 100 | Parameter ‘O’ GAIN = 100 SCALE = 0 | PAO, Tower1 Make-up, 100,0 |
| 2” Osmonics Turbine No scaling on sensor Connected to ‘P’ | Parameter ‘P’ Scale = 75 ‘K’ Factor = 5 | Parameter ‘P’ GAIN = 5 SCALE = 75 | PAP, Tower1 Bleed, 5,75 |
| 1” Osmonics Turbine No scaling on sensor Connected to ‘S’ | Parameter ‘Q’ Scale = 120 ‘K’ Factor = 2 | Parameter ‘Q’ GAIN = 2 SCALE = 120 | PAQ, Boiler Make-up 2,120 |
| Aquatrac Paddlewheel connected to ‘Q’ In a 4” Line, Sensor Label = 18 | Parameter ‘Q’ Scale = 90 ‘K’ factor = 5 | Parameter ‘Q’ GAIN = 5 SCALE = 90 | PAQ, Process Flow, 5,90 |
| Aquatrac Paddlewheel connected to ‘O’ In a 1” Line, Sensor Label = 30.8 | Parameter ‘O’ Scale = 154 ‘K’ factor = 5 | Parameter ‘O’ GAIN = 5 SCALE = 154 | PAO, Process Flow, 5,154 |

Note: GAIN  	=  Gallons per Contact or Gallons per SCALE pulses

SCALE  	=  Sensor factor, Pulses/Gallon for turbines and paddlewheels

Must be less than 255. If Sensor Factor > 255, correct by increasing gain.

Example: Sensor Factor = 1000, therefore SCALE = 200 & GAIN = 0.2

2.8 Connecting 4-20mA Sensors and Liquid Level Sensors

Loop powered Liquid Level sensors and other loop powered 4-20mA sensors connected to inputs ‘G’ 				through ‘J’ 	require that configuration headers ‘LG’ thru ‘LJ’ be jumpered.

These jumpers 	terminate the current loops with 50 ohms, converting the current loop to a

measurable voltage.

Controllers are shipped with ‘L’ jumpers installed unless the sensor input ‘G’ through ‘J’  input is used 	by an accessory card.

AQUATRAC extra sensor modules mounted on the controller backplate may be connected to inputs ‘G’ through ‘J’. An LG thru LJ  jumper must be removed only on the analog input which connects to the backplate module.   Jumpers on module inputs are removed by Aquatrac if an extra sensor module is supplied with the controller.

2.9 Connecting Flowswitches and Level Switches

Controllers having only one flowswitch, Option F, should connect the switch to the ‘U’ input.

Flowswitches or any other switch or dry contacts which close to indicate an operating state may be connected 	to Status inputs ‘U’ thru ‘X’.

WARNING-DRY CONTACTS

Only ‘Dry’ contacts may be connected into Status Inputs. ‘Dry’ contacts do not have any DC or AC voltage 			connected through them by whatever supplies the contacts, a motor starter, a PLC etc.

Contacts with 120VAC or 24-48VDC on them will fail the controller catastrophically.

If you’re not sure check the contacts in both the open and closed state with a digital voltmeter on both AC 			and DC volts ranges.

2.10 Connecting AC Power, Solenoids and Pumps

CAUTION ELECTRICAL SHOCK HAZARD

Unplug the controller before opening the controller enclosure

and installing or changing any wiring or cabling

Relays 1 thru 5 switch the 120VAC power fused by the 5 Amp controller fuse.

When the Relay NO (Normally Open) contact is powered, the R1 to R5 neon indicator is ON.

Typical LMI and PulsaFeeder chemical feed pumps plug into the controller plug box enclosures

or connect directly to the Relay  terminal blocks.

Do not operate the controller ungrounded. An AC power safety ground is required both to meet electrical codes and for measurement accuracy.  An ungrounded controller will fail FlexNET communications.

CABLING CAUTION: Do not connect seven strand AWG14 cable directly to the controller terminal blocks. Bridged strands and loose connections will result. Use either a butt splice to stranded AWG 18 or use multiple stranded AWG14. Controller fusing is code compliant using AWG 18 cable.

2.11 Connecting Alarms and Motorized Valves

CAUTION ELECTRICAL SHOCK HAZARD

Unplug the controller before opening the controller enclosure

and installing or changing any wiring or cabling

120VAC Motorized valves require three wires, Power Open ( Labeled NO ), Power Close

(  Labeled NC ), and Neutral ( Labeled N ).

ALARMING PUMPS & VALVES

Sensors, watermeters and flowswitches can cause dial-outs and alarm relay trips but they will NOT turn OFF relays. Only one-time actuation or daily time-outs can turn OFF relays controlling pumps & valves.

2.12 Connecting a Serial Cables, Telephone Modem or Controller Network

RS232 Serial Connections

Controllers with the R2 option can be connected to a notebook PC for a monthly or weekly system check and 	report download.  Controllers can also be continuously connected to an on-site PC using the RS232 port on the 	right side of the controller enclosure.

Continuous connection to an on-site PC does not prevent controller Modem access

The controller communicates at 9600 Baud, which limits serial cable length from 100 to 250ft. depending on cable type. Longer distances require RS232 to RS422 converters at both ends of the serial cable. RS232-422 converters are available from AQUATRAC INSTRUMENTS.

Connect a DB9 male cable to the DB9 female connector on the right, top side of the controller enclosure.

The RS232 cable may be extended up to 250ft. to a remote PC by connecting Pins 2 to2, 3 to 3 and 5 to 5 and each end of the DB9, male-female cable

Telephone Modem

Controllers with the RM option can be connected to a telephone line and remotely monitored and controlled.

A telephone service similar to one required for a FAX or an extension on the existing telephone system which 	allows direct modem connection is all that’s required.

Have the telephone service terminated in a modular jack beside the controller enclosure and route a 	telephone cable with male jacks on both ends between the modular jack and the LINE modem jack.

Do not plug a telephone service into the telephone jack on the door mounted circuit board.

Controller failure will occur. This connector is not use for telephone-modem communications.

Controller-to-Controller FlexNET Cabling

Controllers with the NT option can be linked together in master-slave networks. If your controller has the NT, networking option, the FlexNET manual will be included with this operating manual within the same binder.

Daisy chain a single pair, shielded AWG22 cable between all of the controllers in the network.

Controller-to-LAN Ethernet Cabling

Controllers with the LN option can be directly connected to a 10BaseT, TCP-IP Ethernet LAN. If your controller 	has the LN option, a serial port-to-LAN converter will be installed in the back of the controller.

Before cabling into your LAN, connect serially to the LAN converter using Trackster LN and set the IP address 	to the one provided by the site network administrator.

Do not connect to the site LAN without setting the IP address. An address conflict may fault the LAN, 	making you very unpopular.

3. COMMISSIONING

3.1  Set-up the controller

After you’ve connected the flowswitch(es), water meters and sensors to the controller, plug in the controller but 	don’t plug in bleed solenoid and chemical pumps until you’ve set-up 	the controller.

See Appendix ‘B’ for the TV Remote keypad navigation and key functions.

1. GET YOUR  TV REMOTE PASSWORD

Open the controller enclosure.

The controller passwords are on a removable sticker on the enclosure, hinge side sidewall

The three digit Level 3 password is 123 and allows viewing of operating levels only.

The six digit Level 2 password is 123456 and is required for setpoint adjustment.

2. SIGN ON USING THE REMOTE KEYPAD

Press Power followed by the six digit password & Enter,

You’ll see  Password Verified. Level 2 access

Press Enter & use channel up & down to scroll through all the sensors, water meters, pumps and solenoids.

3. CALIBRATE  SENSORS AND WATER METERS

Press Enter again & you’ll be at the top of the main menu, ADJUST SETPOINTS?

Press Channel DOWN until Calibrate Sensors? is displayed, then press Enter

Calibrate your Conductivity, pH, temperature and level sensors and water meters by using Channel UP & 			Channel DOWN to scroll through all of the installed sensors.

Key Enter to select the desired sensor or water meter.

Press Enter at the Key Current Value? to single point calibrate; recommended for most sensors.

See Section 4.10 for calibration details on each sensor type.

See Section 4.10, Calibrate Water Meters for details on water meter set-up.

Press Enter to accept your Calibration then Power to end Calibration.

4. ADJUST YOUR SETPOINTS

Adjust Setpoints? is the top of the menu. When it’s displayed, press Enter

Set your Conductivity, pH, inhibitor pump setpoints by using Channel UP & Channel DOWN to scroll 					through all of the controller outputs.

See Section 4.4 for Setpoint adjustment details.

Press Power to end Adjust Setpoints.

5. SET YOUR BIOTIMING  / If you’re not feeding biocides, skip this section

Press Channel UP until Adjust Biotiming ? is displayed, then press Enter

Select each biocide pump relay by using Channel UP & Channel DOWN then press Enter

Key in the Day, then the Hour you want to turn on the biocide pump then key in the time you want the pump 			to run.    	Press Power to escape Biotiming.

6.	SELECT YOUR INHIBITOR CONTROL MODE

Press Channel UP until Adjust Inhibitor ? is displayed then press Enter

Use Channel UP & DOWN to scroll through all relays which control inhibitor pumps, then press Enter

to select your Inhibitor Pump.

You can choose from Bleed & Feed,  Bleed then Feed, Water Meter and Percentage Time for inhibitor 			feed control.  See Section 4.14 for Inhibitor Feed details.

7. ADJUST ALARMS

More Information: The controller response to alarms is detailed in Section 4.8

The controller has time-out, feed limit alarms set on start-up.

If you’re feeding acid or inhibitor based on make-up you’ll want to adjust these alarms.

Press Channel UP until Adjust Alarms ? is displayed, then press Enter

Select which alarm by using Channel UP & Channel DOWN to scroll through each sensor and relay.

Key in new HI and LOW alarm setpoints and Enter

Press Power to escape Alarms.

8. PRIME PUMPS, VERIFY VALVES & SOLENOIDS

CAUTION: Pumps & Solenoids will turn ON. Verify that all pump tubing is connected and sealed

& that electrical connections are completed BEFORE continuing.

Plug chemical pumps and bleed solenoids/valves into the power box at the end of the blue conduit.

Press Channel UP until Prime Pumps ? is displayed, then press Enter

Select which pump or solenoid/valve by using Channel UP & Channel DOWN to scroll through each relay 				& press Enter to turn ON for 5 minutes.

Verify that the selected pump is primed and pumping or that the selected valve is opening and bleeding or 				sampling is occurring.

Interlocked and Alarmed pumps will not turn ON until the interlock relay(s) turn OFF or the Alarm is cleared.

If you try to prime a pump that’s interlocked with a flow switch or another relay, you’ll see a message

displayed on the LCD telling you why a prime cannot occur.

Priming can be stopped by using Channel UP to scroll to Clear Alarms ? , pressing Enter twice.

11. SET-UP’S COMPLETE

Your controller’s operating.

Review Sections 4.1 & 4.11 to verify that water meters are measuring correctly and that conductivity and/or 			pH & ORP are controlling.

3.2 QUIK OPERATE

This section is a limited overview

For detailed instructions see Section 4

3.2.1 View what’s happening now

The  display will scroll through all of the operating sensors, water meters, pumps and solenoids, updating the 		screen every 5 seconds. The TV remote keypad may be used to select a parameter and to access the main 		menu..

1. SIGN ON USING THE REMOTE KEYPAD

Press Power followed by the six digit, 123456 password & Enter then Enter again to get to

Adjust Setpoints?, the top of the menu.  		See Appendix ‘B’ & Section 4.3 for the full menu.

2. SELECT WHAT INTERESTS YOU

Press Channel DOWN & Channel UP to scroll through all the parameters and relay displays.

Parameters are A through J are conductivity, pH, ORP, temperature and liquid level sensors.

Enabled sensors are displayed:

| Tower Conductivity 1786. uS E | Sensor Description Current Value Units Connection Point |
| --- | --- |

Parameters are O through Q are water meters. Active water meters are displayed on the screen:

| Tower Make-up 58300 Gal O | Meter Description Current Value Units Connection Point |
| --- | --- |

Parameters are U through X are status or flowswitch inputs.

Active status switches are displayed on the screen:

| Tower Recirculation ON 127.8 U | Flowswitch or Status Description ON¦OFF ON Time,Minutes Connection Point |
| --- | --- |

ON for a flowswitch means there is flow in the sample piping.

ON Time in measured from midnight OR time since flow valved ON, OR time since alarms cleared.

Relays 1 through 5 power chemical pumps and solenoids

Active relays are displayed on the screen:

| Inhibitor Pump ON 12.6 249.3 1 | Pump, Valve or Solenoid Description ON¦OFF ON Time Minutes Today Relay # |
| --- | --- |

ON Time is the minutes ON this actuation. An inhibitor pump could be ON for 2 minutes every 							500 gallons of make-up. A bleed solenoid could be ON typically for 10 minutes unless a valve 							or filter is blocked.

Minutes Today is the number of minutes ON since mid-night.

Each selected display will remain on the screen for 5 minutes unless Channel DOWN & Channel UP 					or Power is pressed

Press Power to exit.  If no key is pressed for 5 minutes, exit occurs automatically

3.2.2 Adjust a Setpoint

1. SIGN ON USING THE REMOTE KEYPAD

Press Power followed by the six digit password & Enter then Enter again to get to

Adjust Setpoints?, the top of the menu.  		See Section 4.3 and Appendix ‘B’ for the full menu.

2. ADJUST YOUR SETPOINTS

Adjust Setpoints? Is menu top & will display first. Key Enter

Select a pump or valve setpoints by using Channel UP & Channel DOWN.

| Inhibitor Pump Adj=Enter Now=Prev 1 | Key Enter to change setpoints OR Key Previous or Last to view current setpoints |
| --- | --- |

Key Power to escape

CURRENT SETPOINTS DISPLAY

Typical Inhibitor Pump

| 250 Gal VOL 45 Sec ON 1 | Gallons of Make-up measured before Seconds ON pump run time Relay#1 |
| --- | --- |

Typical Bleed Solenoid

| 2800 uS ON 2790 uS OFF 2 | Turn ON the bleed at this conductivity Turn OFF the bleed at this conductivity Relay#2 |
| --- | --- |

Press Power to escape

ADJUST SETPOINTS / INHIBITOR PUMP

| 14 Sec ON 1 | Key in pump run time in seconds then key Enter Use Previous or Last to backspace Key Power to escape |
| --- | --- |

| 125 Gal VOL 1 | Key the make-up volume to be measured before run time occurs then key Enter 1 is the Pump Relay# Key Power to escape |
| --- | --- |

ADJUST SETPOINTS / BLEED SOLENOID

| 2250 uS ON 2 | Key in bleed turn ON setpoint then key Enter Use Previous or Last to backspace Key Power to escape |
| --- | --- |

| 2240 uS OFF 2 | Key in bleed turn OFF setpoint then key Enter 2 is the bleed Relay# Key Power to escape |
| --- | --- |

If you wish to leave a setpoint unchanged,

Key Channel Down or Channel Up to go to the other setpoint.

Key Power to escape all setpoint displays.

3.2.3  View what’s causing an alarm

1. SIGN ON USING THE REMOTE KEYPAD

Press Power followed by the six digit password & Enter then Enter again to get to

Adjust Setpoints?, the top of the menu.  		See Section 4.3 and Appendix ‘B’ for the full menu.

2. VIEW ACTIVE ALARMS – only displayed if there are alarms

Press Channel UP until View Active Alarms? is displayed, then press Enter

View each active alarm by using Channel UP & Channel DOWN.

| Cooling Tower pH LO 6.45 pH C | Display the name of the parameter, HI or LO, current value (6.45) ,units (pH) and connection point (C) Key Channel Up or Down |
| --- | --- |

Key Power to escape

3. CLEAR ALARMS

From Adjust Setpoints?, key Channel UP until Clear All Alarms? is displayed, then press Enter

| Clear all Alarms? Y=Enter N=Mute | Clearing alarms ends all biocide feeds, clears all owed time on inhibitor, ends priming KeyPower to escape |
| --- | --- |

Note: Clearing an alarm without correcting the problem which caused the

alarm will cause the alarm to recur.

3.2.4   Calibrate a Sensor

1. SIGN ON USING THE REMOTE KEYPAD

Press Power followed by the six digit password & Enter then Enter again to get to

Adjust Setpoints?, the top of the menu.  		See Section 4.3 and Appendix ‘B’ for the full menu.

2. CALIBRATE YOUR SENSORS AND WATER METERS

Press Channel DOWN until Calibrate ? is displayed, then press Enter

Select the sensor to calibrate by using the Channel UP & Channel DOWN  & Enter

| Tower Conductivity CAL=Enter NOW=Prev E | Key Enter to Calibrate or Channel UP or DOWN to view other sensors & watermeters. Key Previous for current calibration parameters. Power to Escape |
| --- | --- |

Use the current values to calibrate conductivities, pHs, ORPs and temperatures.

All other sensors require two operating points for calibration.

| Key Current Value? YES=Enter NO=Mute | Key Enter to single point calibrate. Key Mute for 2 point calibration. Power to Escape |
| --- | --- |

| Key Value & Enter _? uS E | Key sensor value then key Enter . Key Mute for decimal point and Prev for backspace. Power to Escape |
| --- | --- |

Displays current units and sensor connection location, ‘A’ to ‘J’

| Offset 10.254 Gain E | Key Enter to accept or Power to abandon See Section 4.10 for expected offsets & gains for each sensor type. |
| --- | --- |

| Sensor Calibrated | After Enter you’ll see this display. Key Power to clear this display. |
| --- | --- |

4. CONFIGURING

4.1 CONTROLLER DISPLAY

Before you sign onto a controller, the LCD will display a new value every 5 seconds.

On Power ON you’ll see an alarm status screen, followed by a software version screen followed by:

Installed & Enabled sensor display:

| Tower Conductivity 1836 uS E | 1st Line = the name of the sensor 2nd Line = current value, units & field wiring location ‘A’ to ‘J’ |
| --- | --- |

Installed & Enabled water meter display:

| Tower Make-up 26410 Gal O | 1st Line = the name of the water meter 2nd Line = volume from midnight, units & field wiring location ‘O’ to ‘Q’ |
| --- | --- |

Installed & Enabled flowswitch, liquid level switch or dry contact display:

| Tower Flowswitch ON 426.2 U | 1st Line = the name of status input 2nd Line = ON or OFF, Minutes ON or OFF & field wiring location ‘U’ to ‘X’ |
| --- | --- |

Installed & Enabled chemical pump, solenoid or valve :

| Inhibitor Pump ON 6.9 1012.3 1 | 1st Line = the name of pump or valve 2nd Line = ON or OFF, Minutes ON this time, Minutes ON from midnight & power relay # ‘1’ to ‘5’ |
| --- | --- |

The scrolling displays show you what’s happening now with the controller and where the various sensors, water meters, flows witches, pumps and solenoids are connected within the controller.

ACTIVE ALARMS

An alarm status screen is displayed on the LCD display as it scrolls.

You can select not to scroll the display on alarm. Refer to the ADJUST SITE SETTINGS? Menu option.

Alarm Display

| 20:07:14 DAY#12 FRI Alarms:SysCQ3 1 | 1st Line = Current Time, Biocide Timer Day# & Day of Week 2nd Line = ‘None’ if no alarms |
| --- | --- |

Each parameter and relay, which alarms is designated by its letter or number.

This example shows alarms on the System, the sensor connected to C, the water meter connected to Q and the pump connected to relay 3.

Only relay time-out alarms can prevent pumps & valves from operating

A System alarm displays as SYS & a Network Slave alarm displays as NET

4.2 ‘TV’ REMOTE KEYS & PROGRAMMING

SAFETY : LCD DISABLED

The LCD & remote keypad are disabled during RS232, Ethernet and modem communications.

Display off because COMPUTER is attached  appears on the LCD.

Staff at the controller is alerted that pumps may be turned ON or solenoids activated and  				 				 local commands cannot conflict with remote commands, confusing both local & remote operators.

KEY SUMMARY

| KEY | SYMBOL | FUNCTION |
| --- | --- | --- |
| Power |  | Attention Press for password entry Escape Abandon current entry and return to previous menu. Exit Command mode & return to 5 second scrolling. |
| Enter |  | Yes Execute the displayed menu option. Execute Enter the displayed numbers as a new Setpoint, Date ,Time, Alarm Level etc..... |
| Mute |  | No Don’t execute the displayed menu option & display the next option . Decimal Keys decimal point in Setpoints & Alarms. |
| Previous Or Last |  | Display the current Setpoint, Biotimer data, Alarm level etc... Backspace or Erase on keying numbers. Rcl, Last & Previous keys provide the same function on different Universal remotes. |
| Channel UP | ( | Display the next Parameter from A thru X and then relay 1 thru 5. Show the previous menu option. |
| Channel DOWN | ( | Display the next Relay 5 thru 1 and then Parameter X thru A. Show the next menu option |
| Volume UP | ( | +Sign Make the Setpoint positive +Scroll Scrolls up thru weekdays on Date & Time set. Scrolls up thru Biotimed Events on each Relay. |
| Volume DOWN | ( | -Sign Make the Setpoint negative -Scroll Scrolls down thru weekdays on Date & Time set. Scrolls down thru Biotimed Events on each Relay. |
| Numeric | 0 – 9 | Numeric entry for Setpoints, dates, times, alarm levels etc... |
| TV |  | Press if no response to initial Power key press |

TURNING ON THE KEYPAD

Press Power	If no response, press TV then Power.

If no response, verify that the power light turns ON when a key is pressed, if not 												replace remote’s batteries.

If controller still does not respond, then verify generic remote is correctly 														programmed, see PROGRAMMING A REMOTE which follows.

Screen responds with password prompt

VIEW ONLY        Key the three digit OBSERVER  Level 3. password then press Enter

ADJUST              Key the six digit    OPERATOR   Level 2. password then press Enter

SCROLLING & HOLDING

After you have keyed the password and the ENTER key Press Channel Up or Channel Down to rapidly 			scroll through a maximum of 14 sensors, flowswitches and watermeters and 5 Relays

.

SELECTING THE MAIN MENU

Press Enter twice at any time after keying in the password or once while scrolling through the parameters and relays.

TURNING OFF THE KEYPAD

Keep pressing Power to exit. The Controller will respond with Goodbye

The controller will automatically exit after five minutes without a key press and return to scrolling thru	 				all enabled relays and parameters , updating every 5 seconds.

PROGRAMMING A REMOTE

SMART ‘AS’ series controllers will work with generic remotes programmed for the most 									common SONY TV’s.

Follow the TV set-up instructions provided with your generic remote starting with the first listed 							SONY TV code.

Press the Power  button after programming, if you view the password prompt, you’ve 									programmed the remote correctly.

If not, reprogram the remote with the second & subsequent SONY TV codes.

Although all generic remotes do not have an Enter key, they will have a key, which provides the Enter 				function.  Similarly the Previous key may be labeled Last or Rcl (Recall).

#### CHANGING BATTERIES

Some versions of TV remotes will require re-programming after changing batteries.

INTERNET SUPPORT

www.aquatrac.com displays pictures of every type of TV remote shipped with the controllers.

Select the SETUP key on your remote picture and you’ll see the SETUP instruction and code.

If the controller fails to respond to a previously functional remote, Press the TV button, then 					the Power button.   If the VCR, CD or AUX buttons are accidentally pressed, the  generic							remote will transmit an incorrect protocol.

4.3 MAIN MENU OPTIONS

After keying the password & Enter, key Enter again & you’ll be at the top of the MAIN MENU,

Press Power to Escape at any time.

ADJUST SETPOINTS? is the top of MAIN MENU. You’ll return to this screen if you key Power.

More than one Power key may be required to return if you are viewing sub-menus.

| ADJUST SETPOINTS? Y=Enter N=Mute | Set & Adjust ON-OFF for pumps and solenoids. View current settings. |
| --- | --- |

( (    Press Up or Down Channel  for next function

| VIEW ACTIVE ALARMS? Y=Enter N=Mute | Only displayed if there are active alarms |
| --- | --- |

( or Press Up Channel   (  for previous option

| CLEAR ALARMS? Y=Enter N=Mute | Ends biocide timing, lockouts & prebleeds. End Priming and owed time on inhibitor pumps. |
| --- | --- |

( or Press Up Channel   (  for previous option

| ADJUST ALARMS? Y=Enter N=Mute | High and low alarms on sensors Feed limit timers on pumps and limit alarms on solenoids |
| --- | --- |

( or Press Up Channel   (  for previous option

| ADJUST DATE & TIME? Y=Enter N=Mute | Clears date logs. Resets biocide Day #1 to most recent Sunday |
| --- | --- |

( or Press Up Channel   (  for previous option

| CALIBRATE SENSORS? Y=Enter N=Mute | Single point conductivity, pH, ORP & Temperature Set water meter gallons/contact or pulses/gallon Adjust tank levels. |
| --- | --- |

( or Press Up Channel   (  for previous option

| VIEW WATER METERS? Y=Enter N=Mute | Gallons to date for this year and last year. |
| --- | --- |

( or Press Up Channel   (  for previous option

| PRIME PUMPS? Y=Enter N=Mute | Adds 5 minutes of ON time to a pump or valve. Use CLEAR ALARMS to end. Displays fault message if no flow or interlocked. |
| --- | --- |

( or Press Up Channel   (  for previous option

| BIOCIDE LOCKOUT? Y=Enter N=Mute | Prevents bleed after biocide feed OR Pre-bleeds before biocide feed. |
| --- | --- |

( or Press Up Channel   (  for previous option

| ADJUST BIOTIMING? Y=Enter N=Mute | Set start day 1-28, start time 00:00 to 23:59 and run time 0-255 minutes. Not displayed if biocide timers not installed |
| --- | --- |

( or Press Up Channel   (  for previous option

| INHIBITOR CONTROL? Y=Enter N=Mute | Select Feed on Meter OR Bleed & Feed OR Bleed then Feed OR % of every 5 Minutes. |
| --- | --- |

( or Press Up Channel   (  for previous option

| ADJUST 4-20mA LOOPS? Y=Enter N=Mute | Adjust & view 4mA and 20mA spans Not displayed if 4-20mA outputs not installed |
| --- | --- |

( or Press Up Channel   (  for previous option

| ADJ.ENABLED PARAMS? Y=Enter N=Mute | Turn ON & OFF unused sensor inputs and pump & valve outputs. View current state; ENABLED or DISABLED |
| --- | --- |

( or Press Up Channel   (  for previous option

| ADJ.SITE SETTINGS? Y=Enter N=Mute | Views installed options, serial number & software version. Turn ON upgrades. |
| --- | --- |

( or Press Up Channel   (  for previous option

4.4 ADJUST SETPOINTS?

Operator password level.

Displayed whenever you key Enter at the ADJUST SETPOINTS? Main menu option

Press Power to Escape this menu

| INHIBITOR PUMP ADJ=Enter NOW=Prev 1 | Key Enter to change setpoints Key Prev or Last to view current settings |
| --- | --- |

( (    Press Up or Down Channel  for next pump or valve

| TOWER BLEED ADJ=Enter NOW=Prev 2 | The number ‘2’ indicates that this setpoint controls relay No.2 |
| --- | --- |

( or Press Up Channel   (  for previous  pump or valve & scroll through all setpoints

ADJ=Enter SUB-MENUS

Displays ON then OFF Setpoints.

Press Enter to execute new Setpoint  or Press Power to Escape Sub - menu

ADJUSTING ON – OFF  SETPOINTS

Bleed solenoid opens at ON and closes at OFF conductivity.

| TOWER BLEED ___4500.___uS ON 2 | Key in a new ON value, using Mute key for decimal point and Previous key for erase or backspace & then Enter. |
| --- | --- |

| TOWER BLEED ___4490.___uS OFF 2 | Key in a new OFF value & Enter to execute. Key Power to escape changing the setpoint. |
| --- | --- |

#### ADJUSTING PUMP TIME & VOLUME

After setpoint Gallons are measured, chemical pump turns ON for setpoint seconds.

| INHIBITOR PUMP _25 SEC ON 1 | Key in a new ON time in seconds, using Previous key for backspace & then Enter. |
| --- | --- |

| INHIBITOR PUMP _156 GAL VOL 1 | Key in a new make-up volume in gallons, using Previous key for backspace & then Enter. |
| --- | --- |

PRESS ENTER KEY TOO OFTEN OR KEY A ZERO SETPOINT

| Setpoint is now 0! Power=NO Mute=YES | The controller will prevent you from entering an accidental zero setpoint unless you key Mute |
| --- | --- |

NOW=Prev SUB-MENU - Displays current SETPOINTS

| ___2500.___uS ON ___2490.___uS OFF 2 | Key Power to return ADJUST-NOW option. ‘2’ is the Relay# controlled by the these setpoints. |
| --- | --- |

4.5 ADJUST BIOTIMING?

Operator password level.

Displayed only if Biocides fed on time exist in your controller

.

| BIOCIDE B ADJ=Enter NOW=Prev 4 | Key Enter to adjust biocide timing or Previous to view current biocide timing. ‘4’ is the Relay# controlled by this biotimer |
| --- | --- |

(   Press Down Channel  for next  biocide or Power to escape

If the controller has only one biocide, the 	Down Channel key will not change the display

TIMED BIOCIDES NOW=Prev  DISPLAY

| BIOCIDE B DAY_4 13:30 _90min 4 | Day#1 is always Sunday. Feeds at 1:30PM for 90 minutes. ‘4’ is the Relay# controlled by this biotimer |
| --- | --- |

( or Press Up Channel   (  to view all preset events on this Biocide or Power to escape

TIMED BIOCIDES ADJ=Enter SUB-MENUS

| BIOCIDE B 1-Add 2-Del 3-Edit 4 | Key 1 to add another event, 2 to delete an event or 3 to edit an existing event. Key Power to escape this display |
| --- | --- |

1-Add Sub-Menu

| BIOCIDE B Day2 02:30 25Min 4 | Use Channel UP or DOWN to edit and Volume UP or DOWN to move back & forth across the screen. Key Enter once event is set or Power to Escape |
| --- | --- |

Day 1 is Sunday. Controllers are shipped with 28 Day biocide timers, so Days 1,8,15 & 22 are the Sundays of weeks one to four.  The start time is 24 hour military format so 16:00 is 4:00PM.

The duration, biocide pump ON time, is set in minutes.

1-Add Sub-Menu continued

Up to 28 events may be set for each biocide pump.

28 Day BioTiming Cycle – Repeats Every 28 Days: Factory Default

If you key Enter, you’ll have the option of selecting the number of times in 28 days the biocide event occurs:

| 1)Weekly 2)Alt.Weeks 3)AltDays4)Once | Key 1,2,3 or 4 to select how often you wish the feed event to occur. Key Power to Escape |
| --- | --- |

FEEDING WEEKLY

Key 1 and a feed event will be programmed for the selected day & time in weeks 1 to 4.

ALTERNATING BIOCIDES

Key 2 and a feed event will be programmed for the selected day and for 14 days later.

Example: Feed Biocide ‘A’ on day 3 (Tuesday) & Key 2, setting events on days 3 & 17.

Feed Biocide ‘B’ on day 10 (Tuesday) & Key 2, setting events on days 10 & 24.

FEEDING DAILY

Key 3 and a feed event will be programmed for the selected day and for every other day.

Example: Feed Biocide ‘A’ on day 1 (Sunday) & Key 3, setting events on odd numbered days 							1,3,5,…25,27.

Feed Biocide ‘A’ on day 2 (Monday) & Key 3, setting events on even numbered days 					2,4,6…26,28.

7 Day BioTiming Cycle – Repeats Every 7 Days

If you key Enter, you’ll have the option of selecting the number of times in 7 days the biocide event occurs:

| 1)Weekly 2)Daily 3)AltDays 4)Once | Key 1,2,3 or 4 to select how often you wish the feed event to occur. Key Power to Escape |
| --- | --- |

FEEDING Weekly is the same as Once, adding a single event at the selected time.

FEEDING Daily adds seven events, one on each day 1 to 7.

FEEDING AltDays adds four events. If you set an event on an EVEN day, you get events on days 2,4,6 & 1. If you set and event on an ODD day, you get events on days 1,3,5 & 7

| Event Updated | The feed times & days you selected have been set. Key Power to Escape this screen |
| --- | --- |

If you attempt to set more than 28 events, you’ll get an error message & the events will not be set

Use the Delete option to remove unused or unwanted events.

2-Delete Sub-Menu

( or Press Up Channel   ( .to select the event you wish to delete

| BIOCIDE 2 DAY10 01:45 180min 5 | Key Enter to delete the displayed event or Power to escape. Key Power to escape ‘Timed event deleted’ display |
| --- | --- |

3-Edit Sub-Menu

( or Press Up Channel   ( .to select the event you wish to edit, then press Enter

| BIOCIDE A DAY15 04:30 180min 3 | Use Channel UP or DOWN to edit and Volume UP or DOWN to move back & forth across the screen. Key Enter once event edited or Power to Escape |
| --- | --- |

The Event Updated message appears after the controller has processed your editing.

4.6 VIEW ACTIVE ALARMS?

Observer & Operator password levels.

View Active Alarms not displayed unless there is an active alarm.

| Cooling Tower pH HI ___8.68 pH C | Displays the current value of the sensor connected to input ‘C’ Key Channel UP or DOWN for other active alarms. |
| --- | --- |

| Tower Bleed HI ___184.6 min 2 | Displays the current ON time of the #2 relay which powers the bleed solenoid. Key Power to escape View Active Alarms |
| --- | --- |

SYS, displays one of a number of possible System Alarm messages.

4.7 CLEAR ALARMS?

Observer & Operator password levels.

| CLEAR ALL ALARMS? Y=Enter N=Mute | Resets the alarm relay, ends biocide events and bleed lockouts, removes Inhibitor pump owed time Key Enter for Yes or Mute for No |
| --- | --- |

After another prompt message and an Enter key, all alarms are cleared and a notification message is displayed. Press Power to clear the message.

4.8 ADJUST ALARMS?

Operator password level.

| Tower Temperature ADJ=Enter NOW=Prev A | Key Enter to Adjust the alarm for the sensor connected to input ‘A’ or Previous to view the current alarm settings. Key Power to escape. |
| --- | --- |

(   Press Down Channel  for next  enabled Sensor, Watermeter, Flowswitch or Relay

ADJUST ALARMS ADJ=Enter SUB-MENUS

ADJUST A  SENSOR-WATERMETER-FLOWSWITCH ALARM

| Tower pH _8.8 HI C | Key high alarm point for sensor connected to ‘C’ input & Enter. Use Previous to backspace & Mute if a decimal point is required. Key Power to escape. |
| --- | --- |

( or Press Channel Down   for LO Alarm

| Tower pH _6.5 LO C | Key low alarm point for sensor connected to ‘C’ input & Enter. Key Power to escape. |
| --- | --- |

Alarms on sensors do not prevent pump, valves and solenoids from operating

ADJUST A  PUMP OR SOLENOID FEED LIMIT TIMERS

| Acid Pump _60 Minutes ON 3 | Key minutes ON at any one time for the pump connected to Relay ‘3’ & Enter. Use Previous to backspace Key Power to escape. |
| --- | --- |

( or Press Channel   Down for Minutes per Day Alarm

| Acid Pump 520 Min. per Day 3 | Key minutes ON in any day for the pump connected to Relay ‘3’ & Enter. Use Previous to backspace Key Power to escape. |
| --- | --- |

Feed Limit Timers work differently for different controls:

Inhibitors:  		Alarm stops feed. Feed restarts at next feed interval.

Bleeds:   		Alarm occurs but bleed doe not stop.

Acid, Oxidant & Biocides: Pump or Solenoid turns OFF and stays OFF until alarm cleared.

Sensors, watermeters and flowswitches can cause dial-outs and alarm relay trips but they will NOT turn OFF relays. Only one-time actuation or daily time-outs can turn OFF relays controlling pumps & valves.

WARNING: Relays may be set to lock OFF or remain operating on alarm time-out

Once a relay has alarmed OFF, Control Equations & Timed Events cannot turn the Relay ON until alarms are reset. Bleed Relays set to ON on alarm will continue to operate independent of time-out settings.

ADJUST ALARMS NOW=Prev SUB-MENU

| 600.0 Min. per Day 240.0 Min ON 4 | Displays the current feed limit or alarm setpoints. Sample screen shows Relay ‘4’ limit timers Key Power to escape. |
| --- | --- |

4.9 ADJUST DATE & TIME?

Operator password level.

WARNING:   Changing the time & date clears all logged and stored operating data.              .

| VOL-Field CHN-Value mm/dd/yy MON13:24:38 | Use Channel UP or DOWN to edit and Volume UP or DOWN to move back & forth across the screen. Key Enter once time set. Power to Escape |
| --- | --- |

4.10 CALIBRATE SENSORS?

Operator password level.

| Tower Conductivity CAL=Enter NOW=Prev E | Key Enter to Calibrate or Channel UP or DOWN to view other sensors & watermeters. Key Previous to view current settings Power to Escape |
| --- | --- |

| Tower Make-up CAL=Enter NOW=Prev O | The letter in the bottom right of the screen indicates the field wiring terminals, ‘O’, for this meter or sensor Power to Escape |
| --- | --- |

CALIBRATE  CAL=Enter SUB-MENUS

for Conductivity, ORP, pH  & Temperature Sensors.

Conductivity, ORP, pH sensors and the temperature sensors connected to ‘A’ input may be single point calibrated using the current value at the sensor.

WARNING: Boiler Blowdowns

Conductivities used for sampling boiler blowdown control will force an immediate SAMPLE and WAIT-to-MEASURE sequence with calibration occurring at the end of the WAIT-to-MEASURE interval

Do not remove the sensor from the sample piping or tank when using Key Current Value?,  single point calibration.

| Key Current Value? YES=Enter NO=Mute | Key Enter for single point calibration or Mute for two point. Power to Escape |
| --- | --- |

SETTING TANK LEVEL

Controllers with the FV: Feed Verification Option use Calibrate & Key Current Value for setting tank or drum level after filling.

Sample the process and measure the pH, conductivity or ORP.

The letter in the bottom corner of the display shows you controller terminal where the sensor is connected.

Sensor Input ‘E’ in the following example.

| Key Value & ENTER ___2240.___uS E | Key current sensor value & then ENTER. Use PREVious for backspace & MUTE for decimal point. Power to Escape |
| --- | --- |

After you enter the current value, the controller will calculate a new OFFSET & GAIN

| _____0.000 OFFSET ____11.456 GAIN E | Key ENTER to accept this calibration or Power to Escape & abandon the calibration |
| --- | --- |

Typical Sensor OFFSETS & GAINS: Single point calibration adjusts the OFFSET or GAIN

| Sensor Type | Range | Notes |
| --- | --- | --- |
| Conductivity – Cooling Tower | GAIN 8-14 | OFFSET always 0.00 Increasing GAIN indicates fouling |
| PH – Cooling Tower | OFFSET 6-8 | GAIN always 0.017 Flat faced & low temp sensors will function with wider offsets. |
| ORP | OFFSET +/-50 | GAIN always –1 Increasing offsets indicate need to clean sensor Platinum band. |
| TEMPERATURE | OFFSET –430 to -480 | GAIN always 0.36 |
| Feed Verification- Tank Inventory | OFFSET 0-1000 | GAIN always 0.00 OFFSET = current tank level in Gallons or Liters |

| Sensor Calibrated | If you accepted the calibration, you’ll see this confirmation. Key Power to clear screen |
| --- | --- |

CALIBRATE  Two Point Calibration SUB-MENUS for Sensors ‘A’ thru ‘J’

Two point calibration is usually only used for Condensate sensors, 4-20mA sensor inputs and for liquid level sensors.  There is no increase in accuracy in water treatment controllers using two point calibration on conductivity, pH, ORP, Temperature…

If you are calibrating a 4-20mA current loop, First Position would be 4mA and Second Position would be 20mA. If a level sensor, First Position would be in air and Second Position would be immersed.

| Put sensor in first Position,press ENTER | Place sensor or current loop at first level & key ENTER Key Power to escape |
| --- | --- |

| Checking sensor Wait one moment | Controller is measuring sensor value |
| --- | --- |

| Key 1st point & ENTER 250 | Key the sensor value which corresponds to the first position & key ENTER. MUTE inserts a decimal point. PREVious is the backspace key. Power to escape |
| --- | --- |

| Put sensor in second Position,press ENTER | Place sensor or current loop at first level & key ENTER Key Power escape |
| --- | --- |

| Checking sensor Wait one moment | Controller is measuring sensor value |
| --- | --- |

| Key 2nd point & ENTER 0 | Key the sensor value which corresponds to the second position & key ENTER. Power to escape |
| --- | --- |

After you enter the current value, the controller will calculate a new OFFSET & GAIN

OR Display an error message.

| ___-12.652 OFFSET _____6.456 GAIN E | Key ENTER to accept this calibration or Power to Escape & abandon the calibration |
| --- | --- |

| Error placing sensor probes | Calibration fails. Controller did not measure a significant difference between first & second positions Key Power to clear screen |
| --- | --- |

| Sensor Calibrated | If you accepted the calibration, you’ll see this confirmation. Key Power to clear screen |
| --- | --- |

CALIBRATE  SUB-MENUS for Water Meters ‘O’ thru ‘Q’

Displays Pulses/Gallon then Gallons/Contact  values.  Water Meter# displayed as last letter of display.

or Press Power to Escape Sub - menu

Insertion Paddlewheels and In-Line Turbines require Refer Scaling to convert pulses/gallon to Gallons

| Key scaling & Enter _58 | Key 0 & Enter if Contact Head meter Key a number between 1 & 255 & Enter if Paddlewheel Key Power to escape |
| --- | --- |

Scaling is the pulses/gallon prescaler used with paddlewheel & turbine meters

Typical Scaling & ‘K’ factors for common paddlewheel & turbine meters:

| Watermeter Type | scaling | ‘K’ Factor | Notes |
| --- | --- | --- | --- |
| Seametrics 3/4”, PVC | 180 | 0.5 | Nominal values only |
| Seametrics 1”, PVC | 210 | 1 | Actual scaling factor on meter body. |
| Seametrics 1 1/2”, PVC | 50 | 1 |  |
| Seametrics 2”, PVC | 30 | 1 |  |
| Seametrics 3”, PVC | 20 | 1 |  |
| Seametrics 4”, PVC | 19 | 1 |  |
| Osmonics 1” Turbine | 120 | 2 | Wiring color code differs for Osmonics |
| Osmonics 2” Turbine | 75 | 5 | Manual shows Seametrics color coding |

| Key K Factor & Enter _50 | Key Gallons/Contact if Contact head meter & Enter Key Gallons/Scaling if Paddlewheel & Enter Key Power to clear screen |
| --- | --- |

Press Enter  after keying in Gallons per Contact or  Gallons per ‘Scaling’ for Turbines & Paddlewheels

Key in new values, using Mute key for decimal point and Previous key for erase or backspace.

CALIBRATE Previous SUB-MENU - Displays current OFFSET & GAIN

Parameter  displayed as last letter of display.

| 120 SCALING 12.500 GAIN O | Meter ‘O’ will measure 12.5 Gallons for every 120 pluses. This meter is a turbine with 9.6 pulses/Gal. Key Power to clear screen |
| --- | --- |

Press Power to Escape Sub – menu or Enter to accept new values.

4.11 VIEW WATER METERS?

Service & Operator password levels.

Displays year-to-date gallons & days operating

| Tower Make-up 01=_86040GAL_210DY O | Displays Gallons to date for year ‘01’ after 210 Days on water meter connected to input ‘O’ Key PREVious for last year or POWER to exit |
| --- | --- |

- Press Down Channel  for next  Water Meter

| Tower Bleed 01=_21050GAL_210DY P | Displays Gallons to date for year ‘01’ after 210 Days on water meter connected to input ‘P’ Key PREVious for last year or POWER to exit |
| --- | --- |

( or Press Up Channel   (  for previous Water Meter

WATER METER Previous SUB-MENU - Displays Previous Year

| Tower Make-up 00=376800GAL_365DY O | Displays Gallons to date for year ‘00’ after 365 Days on water meter connected to input ‘O’ Key PREVious for last year or POWER to exit |
| --- | --- |

4.12 PRIME PUMPS?

Operator password level.

Enter turns on Relay for 5 minutes				Relay# displayed as last letter of display.

If relay is interlocked with a flowswitch or another relay, you’ll see an error message.

| Inhibitor Pump PRIME = Enter 1 | Power to Escape Press Down Channel for next pump, valve or solenoid |
| --- | --- |

| Tower Bleed PRIME = Enter 2 | Power to Escape Use CLEAR ALARMS? To end priming time. Prime again for 10 minutes of ON time. |
| --- | --- |

4.13 BIOCIDE LOCKOUT?

Operator password level.

Lockout turns OFF the bleed solenoid for the Lock-out period in minutes starting at the same time as the Biocide Pump.

Prebleed time in minutes turns ON the Bleed relay before the Biocide Relay to lower the tower conductivity and prevent make-up during biocide treatment.

| Biocide Lockout NEW=Enter NOW=Prev | Power to Escape |
| --- | --- |

BIOCIDE LOCKOUT Enter SUB-MENU

| Select Relay #3 Biocide A | Press Down or Up Channel to view all enabled biocide timers. #3 is the relay powering the pump Press Enter key OR Press Power to escape. |
| --- | --- |

| Biocide A 1-LOCKOUT 2-PREBLEED | Key 1 or 2 or press Power to escape |
| --- | --- |

LOCKOUT DISPLAY

| #2 Locked out on #3 _90 Minutes | The Bleed controlled by Relay #2 will be locked out by the Biocide Pump on Relay #3 for 90 minutes. Key your Lockout time then Enter |
| --- | --- |

Previous key can be used to backspace & correct, Power to escape

Lockout time occurs after the biocide feed time and is used to allow the biocide time to act.

Do not Lockout heavily loaded towers.

The tower may cycle up into scaling conditions during the Lockout period.

PREBLEED DISPLAY

| #3 Prebled on #2 _35 Minutes | The Bleed controlled by Relay #2 will be turned ON before the Biocide Pump on Relay #3 for 35 minutes. Key your PreBleed time then Enter |
| --- | --- |

Previous key can be used to backspace & correct, Power to escape

Prebleeding lowers the tower conductivity before the biocide feed.

Prebleeding is used to allow the biocide time to act before the tower cycles up to the Bleed 			setpoint.

Do not PreBleed towers that are makeup volume limited or you may run the sump dry and 	shut down the chillers.

BIOCIDE PREBLEED Previous  Display

PREBLEED DISPLAY

| #4 Prebled on #2 25.0 Minutes | The Bleed controlled by Relay #2 will be turned ON before the Biocide Pump on Relay #4 for 25 minutes. Key Power to escape |
| --- | --- |

Key Channel Up or Down to view other Lockouts and/or PreBleeds

LOCKOUT DISPLAY

| #2 Lockout on #3 240.0 Minutes | The Bleed controlled by Relay #2 will be locked out by the Biocide Pump on Relay #3 for 240 minutes. Key Power to escape |
| --- | --- |

4.14 INHIBITOR CONTROL?

Operator password level.

Relay# displayed as last letter of display or Press Power to Escape Sub-Menu

| Inhibitor Pump NEW=Enter NOW=Prev 1 | Key Enter to change feed mode or Previous to view current feed mode. Key Power to escape. |
| --- | --- |

Key Channel Up or Down to view other enabled Inhibitor feeds.

INHIBITOR FEED Enter SUB-MENU

You’ll be prompted with four control mode choices.

| Bleed & Feed 1 on 2 YES=Enter NO=Mute 1 | Press Enter to select and Mute to reject and view the next feed option. Press Power to escape |
| --- | --- |

This option turns ON the inhibitor pump connected to Relay 1 when the bleed solenoid connected to Relay 2 turns ON.

Feed limit ADJUST ALARMS? limits the pump operate time.

Use Bleed & Feed when the tower bleeds more than 50% of the time at maximum load.

| Bleed -> Feed 1 on 2 YES=Enter NO=Mute 1 | Press Enter to select and Mute to reject and view the next feed option. Press Power to escape |
| --- | --- |

This option turns ON the inhibitor pump connected to Relay 1 after the bleed solenoid connected to Relay 2 turns ON for the same amount of time that the bleed solenoid was ON.

Feed limit ADJUST ALARMS? limits the pump operate time.

Use Bleed Then Feed for most small cooling towers.

| Feed 1 on Meter O YES=Enter NO=Mute 1 | Press Enter to select and Mute to reject and view the next feed option. Press Power to escape |
| --- | --- |

This option turns ON the inhibitor pump connected to Relay 1 after the water meter connected to input ‘O’ has measured a user set number of gallons.

Use the ADJUST SETPOINTS menu option to adjust the pump ON time and the number of Gallons.

| Percentage Time? YES=Enter NO=Mute 1 | Press Enter to select and Mute to reject and view the next feed option. Press Power to escape |
| --- | --- |

This option turns ON the inhibitor feed pump for a percentage of five minutes.

Press the Enter key to view the time entry sub-menu below

Use this feed mode to ‘base feed’ chemicals.

Percentage Time ON Time

| Key ON time & ENTER ___ Seconds | ON time starts on the five minute mark, turning the inhibitor pump ON for up to 300 seconds every 5 minutes. Press Power to escape |
| --- | --- |

Seconds over 300 turns the Inhibitor Pump ON continuously starting at the next five minute mark.

INHIBITOR FEED Previous  SUB-MENU

Previous will display the current inhibitor control mode.

Bleed & Feed Selected

| Inhibitor Pump Bleed & Feed 1 on 2 | Feeds inhibitor on Relay 1 Pump any time Relay 2 Bleed turns ON Key Power to escape. |
| --- | --- |

Bleed then Feed Selected

| Inhibitor Pump Bleed -> Feed 1 on 2 | Feeds inhibitor on Relay 1 Pump after Bleed Solenoid on Relay 2 turns OFF for the same amount of time that the Bleed Solenoid was ON. |
| --- | --- |

Water Meter Feed Selected

| Inhibitor Pump Feed 1 on Meter O | Feeds inhibitor on the Pump connected to Relay 1 based on the volume of flow through water meter ‘O’ Power to escape. |
| --- | --- |

Percentage Time Selected

| Inhibitor Pump Feed 1 on 25.3% | Turns ON Relay#1 for 25.3% (76 seconds) of five minutes, starting every five minutes . Power to escape. |
| --- | --- |

4.15 ADJUST 4-20mA LOOPS?

Operator password level.

From zero to four 4-20mA output cards may be installed in your controller.

| Tower pH ENT=Adj PREV=Now DA1 | Key Enter to Adjust span or Previous to view present 4 & 20mA span on Digital-to-Analog DA1 Key Power to escape. |
| --- | --- |

Press Up or Down Channel  for next  Digital-to-Analog (DA) Output

| Tower Conductivity ENT=Adj PREV=Now DA2 | Key Enter to Adjust span or Previous to view present 4 & 20mA span on Digital-to-Analog DA2 Key Power to escape. |
| --- | --- |

DC isolated, 4-20mA Current Loops can be used to drive variable speed pumps or to monitor controller conductivity, temperature, liquid level pH or ORP.

Control is PI, with the Proportional set by the user set span and Integral set by the data update rate, 					about once every 8 seconds.

The current loop drivers are pre-calibrated, mounted on the controller enclosure backplate and are labeled #1 through #4. Typically Loop#1 = ACID, Loop#2 = CAUSTIC  &  Loop#3 = CONDUCTIVITY

Connect the current loop cable to the + I - , green, field wiring terminals on the current loop driver card.

ADJUST 4-20mA Loops Enter SUB-MENU

| Enter 4mA Level DA3 ___ 4mA | Key in a 4mA level, using Mute key for decimal point and Previous key for erase or backspace Then key Enter Key Power to escape. |
| --- | --- |

| Enter 20mA Level DA3 ___ 20mA | Key in a 20mA level, using Mute key for decimal point and Previous key for erase or backspace Then key Enter Key Power to escape. |
| --- | --- |

Current 4-20mA Loops Previous SUB-MENU

| 12.500 20mA ___7.000 4mA DA1 | Displays current span for DA1 in the units used for sensors used to control the 4-20mA current loop. Key Power to escape. |
| --- | --- |

4.16 ADJ.ENABLED PARAMS?

Operator password level.

| ADJ.ENABLED PARAMS? Y=Enter N=Mute | Select the sensors, water meters, flow switches and relays, which appear on the LCD display and are used for by the controller. Key Enter to select |
| --- | --- |

ADJUST ENABLED PARAMETERS Enter SUB-MENU

| Acid Pump ENABLED ADJ=Ent 3 | Key Channel Up or Down to view other parameters. Key Enter to Enable or Disable Key Power to escape. |
| --- | --- |

If you attempt to DISABLE a parameter that’s used by the controller, you’ll get one of the following messages. Use the Power key to clear the display.

#### Cannot disable a parameter used as an interlock

Displayed flow switch or dry contacts are used to interlock a pump or valve relay.

Cannot disable param used in relay control

Displayed sensor is used to control a pump or valve relay.

Cannot disable para used in compensation

Displayed temperature is used to thermally compensate a conductivity.

Controllers with the R2 & RM options may modify the controller interlocks, relay controls and thermal compensation to allow disabling of unused parameters.

4.17 ADJ.SITE SETTINGS?

Observer and Operator password levels.

| ADJ.SITE SETTINGS? Y=Enter N=Mute | Displays controller options, upgrades, serial#…. Key Enter to select |
| --- | --- |

( or Press Up Channel   (  for previous option

ADJUST SITE SETTINGS Enter SUB-MENU

| VIEW SITE INFO? Y=Enter N=Mute | Use the Up Channel ( & ( Down Channel keys to view other settings Press Power to escape. |
| --- | --- |

| Scroll LCD on Alarm YES ADJ=ENTER | Key Enter to lock LCD scrolling on alarm. Press Power to escape. |
| --- | --- |

| Daylight Savings? NO ADJ=ENTER | Key Enter to set daylight savings clock option Press Power to escape. |
| --- | --- |

| CONFIGURE PARAMS? Y=Enter N=Mute | Key Enter to re-assign relays, sensors…. Requires written instructions for each re-configuration Press Power to escape. |
| --- | --- |

| UPGRADE CONTROLLER? YES=Enter N=Mute | Key Enter to re-assign relays and sensors. Requires instructions and upgrade codes. Press Power to escape. |
| --- | --- |

| GOTO 7 DAY CYCLE YES=Enter N=Mute | Warning: Deletes all timed events and all relays after Day 7 Press Power to escape. |
| --- | --- |

OR…

| GOTO 28 DAY CYCLE YES=Enter N=Mute | Switches back to Factory Default, 28 day biocide cycle. Press Power to escape. |
| --- | --- |

Use the Up Channel   (   & (   Down Channel  keys

Returns to top of Sub-menu OR Press Power to escape Sub-Menu

ADJUST SITE SETTINGS – Enter on  VIEW SITE INFO?

SITE INFOrmation screens

| SMART AS Ver.4.05 Dual Tower | Controller name, software version and default configuration Press Power to escape. |
| --- | --- |

| Site Name Site Description | User set name & description, requires R2 or RM option to modify |
| --- | --- |

| Serial option ON Modem Option OFF | R2 turns ON RS232 Serial Option & RM turns on RS232 and modem. |
| --- | --- |

| FlexNet Networking Slave Node #2 | Option NT turns ON FlexNET, Master-Slave RS485 networking Display identifies Slave Address or master controller |
| --- | --- |

| Alarm Option ON D/A Driver OFF | Option AD or AR turns ON the alarm relay. Option IC, IP or IO turns ON the D/A Driver |
| --- | --- |

| Controller Serial Number A1994006 | Controller eight alpha-numeric Serial# is required for Upgrades |
| --- | --- |

Use the Up Channel   (   & (   Down Channel  keys to view other settings

5. OPERATION & MAINTENANCE

5.1 ‘Out-of-the-Box’ Operation

Typical controllers are configured as follows.

Your controller may include other functions like biocide timing, corrosion rate, closed loop feeds …

Part Numbers:  SAT-CO… SAT-CP… or SAT-CO-OR…

| Sensor | Connected to: | Controls | Alarms |
| --- | --- | --- | --- |
| Tower1 Temperature pH or ORP Conductivity Flowswitch Inhibitor Feed Bleed | ‘A’ ‘C’ ‘E’ ‘U’ Relay 1 Relay 2 | Interlocks: Relays 1-4 interlocked on Flow switch ‘U’ Relay 2, Bleed Locks out Relays 1,3 & 4 | Enabled on: ‘C’ – pH, 15 min. ’E’ – Conductivity, 120 min ‘1’ – Feed, 30 minutes |
| Tower1 ORP Oxidant Feed | ‘G’ Relay 4 or 5 | Interlocks: Relays 4 or 5 interlocked on Flow switch ‘U’ if either used for Oxidant Control If no pH control, then Relay 3 would be used for oxidant control |  |
|  |  | Conductivity preset to 2000 uS ON, 1975 uS OFF Inhibitor set to feed on water meter ‘O’ | Dial out: OFF Pager: OFF |

5. OPERATION & MAINTENANCE cont.

5.2 Setpoint Guidelines

5.2.1 Conductivity

Set the Turn ON and Turn OFF conductivity control setpoints from 10uS to 50uS apart to keep your 					bleed intervals short.  This method allows you highest inhibitor level control accuracy and minimum 					chemical use in BLEED then FEED  and WATERMETER inhibitor modes.

5.2.2 pH/ORP

Set the deadband between TURN ON & TURN OFF to 0.02pH on acid and caustic setpoints and 5mV 				on ORP controller Oxidant feed setpoints.

A narrow deadband limits undershoot on acid feed and overshoot on oxidant feed.

5.2.3 Inhibitor Control

Controllers offer four inhibitor control methods with the optimum being site and treatment 								program specific.

| Method | Function | Use |
| --- | --- | --- |
| BLEED and FEED | Turns ON the Inhibitor Feed relay whenever the Bleed solenoid or valve in ON | Cooling Towers with restricted bleed lines which bleed more than 50% of the time. |
| BLEED then FEED | Turns ON the Inhibitor Feed relay after the Bleed relay turns OFF for as long as the Bleed relay was ON. | Large chemical savings on towers with poorly located chemical injection locations. |
| WATER METER | Turns ON the Inhibitor Pump for so many seconds after so many gallons of Make-up Interlocked with Bleed relay to deliver Inhibitor after bleed ends. | Precise, load dependent inhibitor feed. Easy to adjust & repeatable. |
| Percent Timer | Turns ON the inhibitor pump for so many seconds every 5 minutes. Interlocked with Bleed relay to deliver Inhibitor after bleed closes. | Use when sensors & meters not available; as a temporary mode during maintenance delays. Use for ‘base-feeding’ |

PERCENTAGE TIME VERIFICATION

Percentage Time always starts exactly on a five minute mark making it easy to verify controller, pump 				operation and timer setting.

5.3 Calibration

Weekly re-calibration of any sensor indicates either a water treatment system out of control, a sensor not 			suited for the application, a wiring or connection error or a sensor fault.

pH ELECTRODES

pH electrodes millivolt per pH output declines slowly over months. A monthly re-calibration is recommended 		for critical control applications. Over time the sensor Offset will increase.  The default offset is -7.00.

An offset 	greater than 7.00 +/- 1 requires an electrode check in a reference buffer solution.

CONDUCTIVITY SENSORS

Conductivity sensors do not drift unless the sensing pins are fouled. Organics and oils can block the   				sensor pins without a visible film. Clean the end of the sensor with a soap and water and a toothbrush or 			isopropyl alcohol if you see the sensor gain increasing each time you calibrate. Typical sensor gain is from 			9 to 14.   Higher gains indicate fouling or sensor pushed too far into the entry ‘T’

5.4 Biocide Timed Events

Timed events are used to feed biocides, dispersants and antifoams.

The controller is shipped in 28 day biotiming mode. Up to 28 events may be set for each 28 day period.

Day 1 is always a Sunday.

BLEED LOCKOUT

Prevents Bleed for a user defined time after every biocide feed event.

Feed biocides during light load periods to prevent high conductivity during the Lockout period.

PREBLEED

Opens the tower bleed for a user set time before each biocide event.

5.5 Alarms

Frequent alarms can indicate actual operating problems with the water treatment system or too many 				alarms set too close to actual operating levels.

Set only those alarms critical to system operation close to the relay ON and OFF control setpoints.

Disable alarms on non-critical alarms.

#### System  Alarms

System alarms are tripped by faults which are not caused by upper and lower alarm levels or time-outs,

System alarms cause two events: An SYS alarm on the LCD and an alarm on the sensor associated with the SYS alarm. Duplicate alarming is required so that fault sources can be identified.

| # | Cause | Associated Parameter Alarm(s) |
| --- | --- | --- |
| 1 | AC Power Outage More Than 1 Hour | AC Power outage of more than one hour has occurred. Data record will be stuffed with ‘*’ asterisks for the time the controller was OFF. |
| 2 | Checksum Failure Reset Setpoints | Back-up battery fault. Occurs after long storage and after commissioning power ON. Controller will revert to manufacturing defaults. Re-program and calibrate. |
| 3 | Feed Pump time limit exceeded | None |
| 4 | Variable Cycles OFF invalid control eqn. | None |
| 5 | Feed Verify OFF, check FV set-up | None |
| 6 | Feed Pump failure feed verify trips | Sets alarm on feed verify meter input. |
| 7 | Conductivity Sensor No.1 Open | Unimplemented |
| 8 |  |  |
| 9 | 12V Power Shorted Wiring Fault | 12 Supply to turbines & paddlewheels or to level sensors shorted to controller common. Clear the short circuit the thermal fuse will recover. |
| 10 | Boiler Blowdown Failure to Sample | Thermal sensor opposite conductivity sensor did not open at end of Sample period. Alarmed also on Status Switch input used for Fail-to-Sample switch. Check for fail to open sample valve, closed manual valves, orifice and needle valves blocked … |
| 11 | Boiler Blowdown Flashing | Conductivity less than 5% of set after end of Sample Period indicates valve did not close or boiler cycling up. Alarmed also on Conductivity Sensor input used for blowdown control. |
| 12 | Corrosion Rate No-Sensor Fault CR Option Only | Controller cannot synchronize with the sensor. Sensor driver may not be installed or may be mis-wired. |
| 13 | Corrosion Rate Overrange Fault CR Option Only | Corrosion currents greater than 150uA. Usually corrosion rates greater than 50mpy. After a visual, confirming look at the corrosion sensor: If you’re feeding acid, check pumps & pH electrode. If it’s a process check for contamination. |
| 14 | Corrosion Rate Pitting Alarm CR Option Only | Pitting indication greater than general corrosion rate. Anodic and cathodic currents of the same polarity indicate that pitting is biasing the corrosion rate measurement. |
| 15 | Corrosion Rate Conductivity Fault CR Option Only | Conductivity too low for corrosion rate compensation. Verify conductivity measurement and remove from calculation if in error. |
| 16 | Network Controller Not Responding NT Option Only | Master cannot talk to Slave via the RS485 FlexNET link. Indicates set-up or communication fault. See FlexNET manual for more detail. |
| 17 | Network Controller Checksum Failure NT Option Only | Garbled or noisy FlexNET communications. Indicates communication fault. See FlexNET manual.. |
| 18 | Network Controller Unexpected Response NT Option Only | Software fault in FlexNET protocol. Indicates unexpected power outage or soft error. See FlexNET manual. |
| 19 | Network Controller Is In Alarmed State NT Option Only | Slave controller alarms to Master. Use AL or NT@ commands to view alarmed Slave# |

5.6 Fault-Cause Summary

The Fault-Cause Summary is separated by type of fault.

The controller technical manual at www.aquatrac.com includes detailed troubleshooting procedures

listed by fault

WARNING - ELECTRICAL SHOCK HAZARD - CONTROLLER DAMAGE

Do not open an outdoor enclosure door if it’s raining, you’ll fail the controller

Opening the enclosure when the controller is ON exposes the 120VAC terminal

blocks on the right hand side of the controller board.

Do not open the enclosure door without unplugging the controller unless

you are competent to work on live controllers.

5.6.1	NO POWER - NO DISPLAY

Open the enclosure door and turn the POWER ON switch on the bottom right of the controller board OFF 				then ON:

1. All five neon RELAY ON lights will flash on power ON and the LCD display will be backlit if the								 controller fuse is OK & there is AC 	power to the controller.

2. WARNING-ELECTRICAL SHOCK HAZARD

Unplug the controller before checking the Fuse located below the POWER ON switch.

Turning the POWER ON switch OFF does not necessarily prevent electrical shock.

Controllers are fused with a Littelfuse 225 series, 2AG size, 5 amp fuse.

Unplug pumps and solenoids before turning the controller ON after fuse replacement & plug 								them in one at time, using the PRIME command to check each one to identify the cause of 								fusing.

3. If the fuse is not blown, verify that the lighting panel and the circuit breaker feeding the

controller plug are ON and that there is 105 VAC to 130 VAC at the bottom, right AC input terminal block.

5.6.2 NO CONDUCTIVITY CONTROL

ALARMED	CLEAR ALARMS to reset the minutes/day time-out alarm on the bleed relay & adjust 							time-out and/or identify trip cause.

An alarm on conductivity Sensor or an alarm on the Bleed Relay will not prevent bleed

Unless the controller has been configured to stop bleed on alarm.

NO FLOW 	Select parameter ‘U’ on the display and verify that it’s ON counting up. Tower 1 bleed 									solenoids are interlocked with the ‘U’ input flowswitch. If the flowswitch contacts are not 									closed, you’ll never bleed.

NO BLEED  Use the remote keypad to PRIME Relay No.2 and verify that the No.2 relay neon light turns

ON and that the bleed valve or solenoid actuates and flow occurs in the bleed line.

Clear Alarms ends priming.

Check for blocked in-line filters and closed isolation valves.

Verify that the sensor is not valved off, bypassed or blocked by throttling valves.

NO READ    If you’re reading a very low conductivity when your testing shows a high conductivity,

remove and clean the conductivity sensor.  Verify that ALL the conductivity wires are firmly 								connected to controller terminal strip.

5.6.3  NO pH or ORP CONTROL

ALARMED	CLEAR ALARMS to reset the time-out alarm on the pump relay & adjust time-out and/or 						identify trip cause.

NO FLOW 	Select parameter ‘U’ on the LCD display and verify that it’s ON & counting up.

Tower 1 Acid, Caustic & Oxidant pumps are usually interlocked with the ‘U’ input

flowswitch. If the flowswitch contacts are not closed, you’ll never pump chemical & you cannot PRIME to check the pump.

NO FEED    Use the remote keypad to PRIME the acid or oxidant pump Relay and verify that the pump 								relay neon light turns ON and pump actuates. CLEAR ALARMS ends priming.

NO READ.   pH’s and ORPs usually change very slowly in cooling water systems.

Solution Grounds: Solution grounds are included with controllers, which include pH/ORP. 		Verify the green solution ground wire is connected to the controller backplate and 					that AC power to the controller is grounded

Offsets that vary more than 20% from the default values indicate either a sensor 											requiring cleaning, a contaminated or an aged sensor.

Verify that ALL the sensor wires are firmly connected to controller terminal strip.

If you shorten the electrode cable : The clear, center conductor on sensor coaxial cable 				has a loose black, conductive shield. Remove the black layer from the center 						conductor if you have shortened to sensor cable.  The black overall coaxial jacket is 				not conductive.

5.6.4 NO BIOCIDE FEED

NO FLOW 	Select parameter ‘U’ on the display and verify that it’s ON & counting up. Biocide pumps									are usually interlocked with the ‘U’ input flowswitch. If the flowswitch contacts are 											not closed, you’ll never pump biocide & you cannot PRIME to check the pump.

NO FEED    Use the remote keypad to PRIME each biocide Relay and verify that the pump

relay Neon light turns ON and pump actuates and biocide flows.

CLEAR ALARMS ends priming.

Tower 1 Biocide pumps are usually interlocked with the Bleed Relay No.2.

ADJUST SETPOINTS on Relay 	No.2 to turn OFF Relay No.2 and allow the BIOCIDE to 	turn ON.

NO SET.      Review the biocide timing to verify the timing, start times and duration are correct for 										each biocide relay.  It’s easy to program Relay No.4 and then plug the biocide pump into 								Relay#5

WRONG DAY#   The first display on Power Up shows the biocide timing Day# and the current time.

Select the ADJUST BIOTIMING on the display menu and press the Previous key

to verify both the feed times and Day#’s

5.6.5 NO TV REMOTE KEYPAD OPERATION

DEAD KEYPAD

TV Not Selected		Press TV again. Accidentally pressing CABLE or VCR turns OFF the remote.

Batteries Removed    If you’ve removed or replaced the batteries, you may have to re-program the 												remote as a SONY TV – See www.aquatrac.com & select TV Remote on the 												home page and select the Set-up key on your remote & you’ll get the 														programming code & method

Dead Batteries			If the visual indicator on the remote does not turn ON or is dim when you 													press a key, replace the batteries and reprogram the remote.

6 PRODUCT SUPPORT

SMART ‘AS’ series controllers are supplied by Aquatrac Instruments Inc.

For accessories, parts and customer support, please have controller part number located immediately below the door mounted circuit board & the serial number of your product available.

Phone:  		 800-909-9283

8:00AM to 5:00PM PST

FAX:	     		909-476-2412

Web:   	   		www.aquatrac.com

Shipping:  	    AQUATRAC INSTRUMENTS

8660 Red Oak.

Rancho Cucamonga, CA

91730

APPENDIX ‘A’ CONTROLLER OPTIONS

& Sensor Part Numbers

The controller part# describes what’s included with your controller

| Part# | Control | Sensors Included | Notes |
| --- | --- | --- | --- |
| SAT | SMART ‘AS’ Cooling Tower |  | Fused 5 Amps |
| CO | 1 Bleed Solenoid/Valve 1 Inhibitor Pump | 1 Conductivity-Temperature Sensor Part# A261200 | Includes 3 water meter inputs |
| PH PH2 | 2 Chemical Pumps 4 Chemical Pumps | pH Sensor pH Sensors Sensor Part# A261100 | Control both acid & caustic |
| CP | 1 Bleed Solenoid/Valve 1 Inhibitor Pump 1 Chemical Pump | 1 Conductivity-Temperature Sensor Part# A261200 1 pH Electrode Sensor Part# A261100 | Includes 3 water meter inputs |
| T1 T2 T3 | 1, 2 or 3 Biocide Chemical Pump |  | Timed events & %Time |
| F | Interlock pumps & valves | Cooling Water Flowswitches Part# A261403 | Required for acid feeding |
| OR OR2 | 1 Chemical Pump 2 Chemical Pumps | 1 ORP Electrode Sensor part# A261105 | Feed above a below an ORP or Feed during a time window |
| LN | Ethernet TCP-IP LAN Support |  | Low levels may be set to alarm High levels may operate a relay |
| L1-L3 |  | 1-3 Liquid Level Sensors | Low levels may be set to alarm High levels may operate a relay |
| IC IP IO | 4-20mA out, conductivity 4-20mA out, pH 4-20mA out, ORP |  | Up to four, 4-20mA/controller Software spanned & assignable. |
| CR | Corrosion Rate Measurement | 1-4 Corrosion Rate sensors | Check on oxidizers & pH control |
| CX | Xtra conductivity measurement | 1 Conductivity sensor | Raw or closed loop conductivity |
| NT | FlexNET RS485 Networking |  | Multiple controller sites |
| R2 | RS232 command & control |  | Serial notebook or PC communication |
| RM | Modem & RS232 command & control |  | Auto-switched Modem & RS232 communication. |
| AD | 1 Control System Alarm Input |  | Contact set to DCS on alarm |
| AR | 1 Light or Audible Alarm |  |  |

APPENDIX ‘B’ TV Remote Keypad

Menu Tree

The TV remote is programmed to be a SONY television.

For programming information see www.auqatrac.com , select Remote Control Config  from the Home page left side menu bar and scroll to your TV remote. Select the Setup button with your mouse & you’ll view the setup method and code.

| KEY | SYMBOL | FUNCTION |
| --- | --- | --- |
| Power |  | Attention Press for password entry Escape Abandon current entry and return to previous menu. Exit Command mode & return to 5 second scrolling. |
| Enter |  | Yes Execute the displayed menu option. Execute Enter the displayed numbers as a new Setpoint, Date ,Time, Alarm Level etc..... |
| Mute |  | No Don’t execute the displayed menu option & display the next option . Decimal Keys decimal point in Setpoints & Alarms. |
| Previous Or Last |  | Display the current Setpoint, Biotimer data, Alarm level etc... Backspace or Erase on keying numbers. Last & Previous keys provide the same function on different Universal remotes. |
| Channel UP | ( | Display the next Parameter from A thru X and then relay 1 thru 5. Show the previous menu option. |
| Channel DOWN | ( | Display the next Relay 5 thru 1 and then Parameter X thru A. Show the next menu option |
| Volume UP | ( | +Sign Make the Setpoint positive +Scroll Scrolls up thru weekdays on Date & Time set. Scrolls up thru Biotimed Events on each Relay. |
| Volume DOWN | ( | -Sign Make the Setpoint negative -Scroll Scrolls down thru weekdays on Date & Time set. Scrolls down thru Biotimed Events on each Relay. |
| Numeric | 0 - 9 | Numeric entry for Setpoints, dates, times, alarm levels etc... |
| TV |  | Press if no response to initial Power key press |

APPENDIX  C  Options Sub-Panel

C1. SERVICES

The Options Sub-Panel contains:

1. The interface cards which allow extra conductivity, pH-ORP and corrosion rate sensors to

connect to controller analog inputs ‘G’ through ‘J’

2.  The driver and  4-20mA output cards. A single 4-20mA requires one driver and one output card. 									Two 4-20mA loops requires a driver and two output cards for a total of three cards.

Any combination of extra sensors and 24VAC drivers up to four cards may be mounted on the Option Sub-Panel.

Optional cards are supplied pre-wired to the relay output or controller parameter input.

C2. LOCATION

The 1/8” thick, PVC or Lexan Sub-Panel is mounted to the controller enclosure aluminum backplate.

Controllers with modems will have the backplate mounted above the modem.

# C3. EXTRA CONDUCTIVITY SENSORS

Controllers with more than one conductivity sensor will have this part.

Added conductivity sensors may be used for closed loops, towers or boiler-tower controllers.

Jumper Configuration

| Use | 50% | Temp |
| --- | --- | --- |
| Cooling Tower | OUT | OUT |
| Boiler Blowdown | IN | IN |
| Condensate | OUT | IN |

C4. EXTRA pH & ORP SENSORS

Controllers with more than one pH or ORP sensor will have this part.

C4. 4-20mA Current Loop Outputs

Controllers with the IC, IO, IP options will have these components

Do not adjust the adjust the Current Loop GAIN & OFFSET potentiometers.

They have been factory calibrated,  The ILOOP manual is provided for hardware reference only.