SMART Flex &

SMART ‘AS‘

Water Treatment Controllers

Technical Manual

Revision 1.2    Issued 12/02

Version 4.3 & later firmware

8660 Red Oak  (  Rancho Cucamonga  (  California   (   91730

www.aquatrac.com

Contents  1 of 2

1.  Overview																										1.1 ‘AS’ & Flex Controllers								5

1.2  Supporting Information Sources				5

2. Trouble Shooting Sequences

2.1 Feed Limit Timers, Fuses, Water Damage	6

2.2 Cooling Tower Conductivity 						7

2.3 Boiler Conductivity									8

2.4 pH Measurement & Control						9

2.5 ORP Measurement & Control 					10

2.6 Water Meter Measurements						11

2.7 Pump-Valve-Solenoid Problems & Alarms	12

3.  Trackster & Trackster-LN																			3.1 Overview													13

3.2 Terminal Mode											13

4. Serial Port & Modem Command Set

4.1 R2-RM Installation & Troubleshooting		14

4.2 Serial Port Command Set							16

4.2.1 SENSOR, WATER METER, 					16

FLOWSWITCH LETTERS & RELAY NUMBERS

4.2.2 COMMAND SYNTAX							16

4.2.3 COMMAND SET									17

4.3 Data streaming, ‘AP’ commands					37

5. Application Notes

5.1 Enclosure Installation								40

5.2 PM Schedule											41

5.3 Rate-to-Volume Conversion & Control 		42

5.3.1 OBJECTIVE										42

5.3.2 TYPICAL APPLICATIONS						42

5.3.3 REQUIRED SOFTWARE						42

5.3.4 INSTALLATION									42

5.3.5 TECHNICAL-OPERATIONAL NOTES		43

5.4 Variable Cycle Special Control					44

5.4.1 OBJECTIVE										44

5.4.2 TYPICAL APPLICATION						44

5.4.3 REQUIRED COMPONENTS					44

5.4.4 INSTALLATION									44

5.4.5 TECHNICAL-OPERATIONAL NOTES		45

5.4.6 COMMAND SYNTAX							45

5.5 Feed Verification Inventory-ppm Tracking	46

5.5.1 OBJECTIVE										46

5.5.2 TYPICAL APPLICATION						46

5.5.3 REQUIRED COMPONENTS					46

5.5.4 INSTALLATION									47

5.5.5 TECHNICAL-OPERATIONAL NOTES		47

5.5.6 COMMAND SYNTAX							50

5.5.7 HYPERTERMINAL SCREEN DISPLAY		51

5.6 Feed Verification Meter Installation			52

5.6.1 OBJECTIVE										52

5.6.2 REQUIRED COMPONENTS					52

5.6.3 INSTALLATION									52

5.6.4 SOFTWARE UPGRADE						52

5.6.5 CABLING & CONTROLLER CONNECT.	53

5.6.6 PUMP SET-UP & VERIFY METER			53

5.7 Time Modulation Control							54

5.7.1 OBJECTIVE										54

### 5.7.2 FUNCTION										54

5.7.3 COMMAND SYNTAX							54

5.7.4 ‘ON’ TIME RESOLUTION 						55

& RECALCULATION

5.7.5 DIAGNOSTIC – ‘ST’ COMMAND			55

5.7.6 LIMITS & OUT-OF-LIMITS RESPONSE	55

5.7.7 ALARMS & DATA LOGGING					55

5.8 Timed Cycling Control								56

5.8.1 OBJECTIVE										56

### 5.8.2 FUNCTION										56

5.8.3 COMMAND SYNTAX							56

5.8.4 CURRENT STATE MONITORING			57

5.8.5 LIMITS & OUT-OF-LIMITS RESPONSE	57

5.8.6 ALARMS & DATA LOGGING				57

5.9 Version 4 ‘AS’ & Flex Controller Software	58

5.9.1 OBJECTIVE										58

5.9.2 NEW COMMAND SUMMARY				58

5.9.3 TRACKSTER SUPPORT						58

5.9.4 CONTROLLER FUNCTION CHANGES		59

5.9.5 NEW in Version 4.3							61

6. Sensor Specifications & Cabling					61

USER WARNING : CAUTION

Water Treatment Controllers operate steam and water valves and may pump hazardous, corrosive and toxic chemicals.

Opening the controller enclosure cover exposes users to the risk of electrical shock at power line voltages.

Understand fully the implications of the control setpoints, chemical feed methods, interlocks and alarms that you select.

Harm to personnel and damage to equipment may result from mis-application.

Unplug or turn OFF the AC power to the controller if you have any concerns regarding safety or incorrect controller operation and notify supervisory staff.

TV Remote Keypad Use

If the Keypad does not respond, press the TV button.

Smart controllers think that they are SONY TV’s

POWER       Escape, used to clear the screen & return to a previous menu

ENTER        Selects the main menu. Used to end any numerical entry

CHANNEL UP/DOWN  Moves up & down, selects, set date & biotimer #’s

VOLUME UP/DOWN    Moves back & forth across the screen

LAST or PREVious    Backspace, used to correct & edit number entry.

1.  Overview

1.1 ‘AS’ & Flex Controllers

The Technical manual details controller functions not covered in the controller Installation and Maintenance manual for the Smart Flex and Smart Automated Service, ‘AS’ series controllers.

Flex & ‘AS’ series controllers only differ in the number of Sensor Inputs and Relay Outputs

Operator functions and the user interface are identical in both controllers.

Flex Controllers: Two pH or ORP, two conductivity and thermal sensors drives are built-in to each controller.

‘AS’ Controllers: One pH or ORP, one conductivity and thermal sensor drive are built-in to each controller.

| Controller Type | Power Relays (1) | Water Meter Inputs (2) | 4-20mA Inputs (3) | 4-20mA Outputs (4) | Dry Contact Inputs (5) | 120VAC Fusing (6) |
| --- | --- | --- | --- | --- | --- | --- |
| Flex | 8 | 3 | 8 | 4 | 6 | 7 amp |
| ‘AS’ | 5 | 6 | 4 | 4 | 4 | 5 amp |

Notes:

- Each controller includes 4 SPDT, NO & NC relays for motorized valves. The controller powers the load pump, valve or solenoid with 120VAC.

- Each water meter input can accept either contact head or three wire paddlewheel & turbine meters in any combination from both two and three wire meters.

- 4-20mA inputs may be used for accessory sensors, extra conductivities, pH’s, ORPs, corrosion rate sensors and/or any user supplied 4-20mA signal.

- Any measured sensor or relay control can be directed towards any of the 4-20mA outputs.

- Used for flowswitches, low level switches, operating interlocks.

- Flex series have a second 1Amp fuse for the controller electronics.

1.2 Supporting Information Sources

Accessories and controller options have dedicated manuals, available at www.aquatrac.com

Controller installation specifications are also available in downloadable formats.

| Option | Accessory – Option | Manual File |
| --- | --- | --- |
| -CR (Steel) -CR/CU (Copper) -CR/AM (Admiralty) | SMART Corr Corrosion Rate Sensor. | LPRMAN3.doc |
| -IC, IO, IP | 4-20 mA Current Loop Driver | LOOPMAN2.doc |
| -L1, L2, L3, L4 or L5 | Liquid Level Sensor | LLS_NM.doc |
| LVS-36, LVS-48 | Liquid Level Switches, 36” & 48” | UG_LVS.doc |
| M2RS485 | RS232 to RS485 Converter Set Extends serial; cable beyond 250ft. in any one building. | RS485.doc |
| MEXTPH | pH Amplifier, Installation & Operation | PHMANA.doc |
| -NT | FlexNET Controller-to-Controller Networking | Netman.doc |
| SAB-TF | Temperature Measurement | SAB-TF.doc |
| Trckstr, Trckstr-LN | Trackster | Trman_20.doc |

2. Trouble Shooting Sequences

2.1 Feed Limit Timers, Fuses, Water Damage

The most common controller faults in order of frequency are:

- Feed Limit Timers

Only feed limit timer alarms, open interlocks and flowswitches, prevent chemical pump from operating.

Alarms on sensors, water meters, flowswitches and system level alarms do not prevent pumps and valves from operating.

‘Clear Alarms’ to restart pumps and valves and refer to section 2.7 Pump-Valve-Solenoid Problems & Alarms

- Blown Fuses

AQUATRAC part ‘FUSES’ contains 10 each of Flex Relay Fuse, AS Controller Fuse and 2Smart or SMART1 fuse for a total of 30 fuses.

All of AQUATRAC’s controller fuses may be purchased from DIGI-KEY, 1-800-344-4539

| Description | DIGI-KEY Part# |
| --- | --- |
| Flex Relay Fuse Littelfuse 2AG 7Amp, 125VAC | F653-ND |
| Flex Control Fuse Littelfuse 2AG 1Amp, 250VAC | F645-ND |
| AS Controller Fuse Littelfuse 2AG 5Amp, 125VAC | F652-ND |
| 2Smart & SMART1 Fuses Littelfuse 3AG 5Amp, 250VAC | F123-ND |

Flex controllers use a separate 7 amp fuse for the relays.

The Flex control electronics are fused with a 1 amp fuse.

# REPLACING FUSES:

Unplug the controller power cord.

If the controller AC power is hardwired, turn OFF the feed circuit breaker.

Verify that the AC power is OFF before removing the open fuse.

If you’re continually blowing fuses, disconnect all pumps, valves and solenoids and reconnect sequentially until you identify the cause of fusing.

WARNING: Controllers are not fused for fractional horsepower pumps.

These pumps require an external motor start relay with 120VAC coil.

- Water Damage

Failure to securely close the enclosure door fails more controllers than miswiring.  Look along the top 	surface of the door mounted circuit board for the signs of water damage Usually a white water hardness 	deposits is visible on electronic components and connectors.

In extreme cases blue copper corrosion products will be visible on the surface of the controller circuit 	board.

A broken flowswitch shaft will leak water up the red flowswitch cable and onto the ‘U’ and or ‘X’ status 	switch inputs.

Water damaged controllers are usually not repairable and require replacement of the controller door 	assembly. If the controller power is ON when the door is wetted, partial or total controller failure will 	occur.

3. Trackster 	& Trackster LN

3.1Overview

Trackster is the Windows user interface software is for controllers with the R2, serial port, RM, Modem & Serial Port and R2-NT, Serial Port & RS485 networking options.

Trackster-LN is used with controllers having the LN option and connected to a TCP-IP, 10BaseT, Ethernet LAN.

Trackster-LN differs only in allowing network IP addresses in addition to the modem phone numbers and serial port connections supported in Trackster.

Passwords:

The configure level password may be changed by Trackster users. If you modify the configure level password 	and then forget the new password, controllers without remote access must be returned to Aquatrac to have the 	password reset.

3.2  Terminal Mode

Version 4.0 control mode configurations are not supported in Trackster 2.31 & earlier.

Trackster Terminal mode is used configure:

Feed Verification, Variable Cycles, Rate-to-Volume and Alarm on No Flow.

Note that when you Enable an unused sensor ‘A’ to ‘N’, in a controller running Version 4.0 and later software, the sensor gain = 1, allowing calibration in Trackster.

Entering Terminal Mode:

When you are connected to the controller at the configure password level using any View:

- Right mouse click on the inhibitor pump or any active valve, pump or solenoid.

- Select Configure Control & left mouse click

- Key Ctrl-Alt-Shift and the Terminal mode window will appear.

- Key Enter to get a password prompt ‘>’

- The serial commands detailed in Section 4.2.3 may now be executed.

- Close the Terminal window to resume normal Trackster operation.

4. Serial Port & Modem Command Set

4.1 R2-RM Installation & Troubleshooting

# 4.1.1 RS232 Serial Port Connections

Controllers with the R2 serial port option, will have a DB9 connector on the outside, top right side of the controller enclosure.  You can connect serially to the controller using a MALE-FEMALE DB9 Cable. NULL modem cables will not communicate.  Set your terminal emulation to VT100.

### Verifying your Serial Cable

You can verify that your cable is not a NULL modem cable by checking for a circuit between pin 2 on each end 	of the cable.  A short or continuity between pin 2 at each end of cable indicates that your cable is pinned correctly and is not a NULL modem cable.  A NULL modem cable crosses pins 2 & 3

Verifying A Serial Port:

You can connect to the controller using a serial utility like Hyperterminal. Hyperterminal is part of 	WINDOWS & is usually accessed from START 	– Programs – Accessories or Accessories-	Communications & Hyperterminal.exe

Select your serial COM Port and set communication parameters to: Bits per Second = 9600, Data bits = 8, 	Parity = none, Stop bits = 1and flow control = none

Ensure that no other software is using the serial port; turn off Palm and PDA applications that auto-synch.

Ensure that the COM port is available and not used for IR communications.

Connect your serial cable to the controller and key Enter, You’ll get a password prompt.

Note that Hyperterminal will tell you that you are connected even if the serial cable is disconnected.

### Extending the RS232 Cable

Controllers communicate at 9600 baud, allowing you to extend the serial cable to 250ft, 75m without a line amplifier.  Use two pair or three conductor, overall shield, AWG22 cable and route that cable away for variable speed drives and motor starters. Do not install the cable in the same conduit as 120VAC power cabling.

Pin the DB9 Male & Female connectors at either end of the cable PIN 2 to PIN 2, PIN 3 to PIN 3 and PIN 5 to PIN 5.

# My Notebook doesn’t have a Serial Port

Newer notebooks, particularly the entry level Toshiba’s & Compaq’s have USB ports but not serial ports.

Purchase a USB-to-Serial DB9 converter from CompUSA or equivalent vendor to convert a USB port to a DB9 port. The newer converters are compact, built into the DB9 connector.

# 4.1.2 Modem Connections

The controller modem is located in the back of the controller enclosure and powered by the controller 120VAC and controller AC line fuse.  Ensure that there are at least two lights are ON on the Modem. 		Some types of modems may have three lights ON.

Verify the there is a serial cable connected form the back of the modem to the door-mounted circuit board DB9 connector.

Perform the following sequence if the modem does not answer the phone:

Modem Power ON?

Verify that the modem push button power switch is ON

Verify that the power jack from the modem power cube is fully inserted into the modem.

Verify and that the modem power cube black & white AC power cables are connected to the controller 	terminal blocks.

Flex connects to a dedicated 2 pin block, terminals tagged LF/Black & N/White

AS connect to terminals labeled LF/Black and any Neutral terminal, N to N5

Flex Series Controllers: The modem is fused with the power relays. If the power relay 7Amp fuse has opened, the modem will be OFF. Prime a pump to verify that one on the neon indicators turns ON to verify that that the relay fuse is OK.

Caution: If you turn the modem power OFF and ON or if the modem power was OFF, switch the controller power OFF then ON to re-initialize the modem.

Phone Connected to Correct Jack?

The telephone jack should be plugged into the modem jack labeled LINE not the jack labeled PHONE.

Dialing to Correct Extension?

Plug a phone into the modem PHONE jack & dial the controller extension. If the phone rings, you have the correct extension. The test phone needs to be one that you would use in a residence. Many proprietary phone systems have phones that won’t work when plugged into a FAX line or a modem PHONE jack.

Controller talking to Modem?

Connect to the controller local serial port using Trackster software.

Right mouse click on the controller icon and select View Configuration

Note that Installed Options shows both Serial Port & Modem

Check the Modem Test result at the bottom of the pop-up;

Modem OK indicates that the failure to answer fault is within the modem – phone line connection.

Modem is not responding indicates that the controller is not communicating with the modem.

There are several possible fixes:

Verify that the serial cable between  back of the modem and the top of the controller 										door is firmly inserted.

Modem serial port failure OR Controller software version less than 3.52 may give a false modem						 error on some modem types.

4.2 Serial Port Command Set

4.2.1 Sensor, Water Meter, Flowswitch Letters & Relay Numbers

Sensor, relay, status switch and water meter inputs are identified by letter & number codes, allowing users to change input names without changing Trackster view operation.

| Inputs & Outputs | Flex Only | Function | Notes |
| --- | --- | --- | --- |
| A |  | Thermal sensor driver | Used with SAB-TF & conductivity sensors A261200 |
| B | Yes | Thermal sensor driver | Identical to ‘A’ |
| C |  | pH or ORP sensors | Used with pH sensors: blue, A261100, flat faced, A261102, & high temp, SNPH-SS OR ORP sensors: red, A261105, flat faced ORP-FF. |
| D | Yes | pH or ORP sensors | Identical to ‘C’ |
| E |  | Conductivity sensor driver | Used with tower conductivity sensors A261200 with blue cable sleeve or boiler sensors A261000, condensate-high pressure A261016 |
| F | Yes | Conductivity sensor driver | Identical to ‘E’ |
| G-J |  | 4-20mA input and accessory cards. | Corrosion rate card inputs. Extra conductivity, pH, ORP cards. User supplied 4-20mA on chemical levels, flow rates, steam demand, pressure … |
| K-N | Yes | 4-20mA input and accessory cards. | Identical to ‘K-N’ |
| O-Q |  | Water meter inputs | Any combination of contact head and paddlewheel-turbines. |
| R-T | Yes | Water meter inputs | Identical to O-Q. |
| Relay 1 |  | SPST 120VAC | Typically an inhibitor pump. |
| Relay 2 & 3 |  | SPDT 120VAC | Tower Bleed & Acid pump OR Boiler 1 & 2 blowdown. |
| Relay 4 & 5 |  | Flex: SPST 120VAC ‘AS’ SPDT 120VAC | Flex: Chemical pumps ‘AS’ Chemical pumps or Boilers 3 & 4 |
| Relay 6 & 7 | Yes | SPDT 120VAC | Typically Chemical pumps or Boilers 3 & 4 |
| Relay 8 | Yes | SPST 120VAC | Typically Chemical pump |

4.2.2 Command Syntax

Spaces are ignored, Sub-commands are always separated by commas,

Example;  PAA,Tower Temp,1.0,0,F

Sets the description, gain, offset & units for PArameter ‘A’

Typing two sequential commas leaves the subcommand unchanged.

Example;  PAE,Raw Water Conductivity ,,, uS

Changes the E parameter description & units but NOT its offset and gain.

Typing the two letter command prompts with command template

Example; PA Enter

Displays:   PA[A..Z], Descriptor, Gain, Offset, Units, Compensation

4.2.3 Command Set

?:  Show  Menu

Explanation of all two letter commands.

Type the 2 letter command & Enter for the command syntax

AL: ALarm

AL [Parameter A..Z], Alarm Relay 1/0,  Dial-out 1/0,  High Alarm,  Low Alarm,  Delay (minutes),

OR

AL [Relay 1..8], Alarm Relay 1/0,  Dial-out 1/0,  Minutes in any actuation,

Minutes in any one Day, Alarm State Response 1/0,

Example:  AL K,  1, 1, 150, 10, 60

For level sensor connected to input ‘K’, turn on the alarm relay and dial out an alarm if  the level is 							above 150 or below 10 for more than 60 minutes.

Example:  AL6,  120 ,1200 ,0  ,0 ,0

If Relay #6 operates for more than 120 minutes at any not time or for more than 1200 minutes in a 							day, turn OFF relay 6, set the alarm relay and dial out an alarm.

AL[A...Z or 1..8]  	Displays the parameter or relay alarm  table

AL@A  				Displays all analog input alarm parameters

AL@F  				Displays all flow meter input alarm parameters

AL@S  				Displays all status input alarm parameters

AL@R  				Displays all relay output alarm parameters

AP: System Command

This command is used only by Trackster & base station software to compress data streams

It is not useable by serial port & modem users. See Section 3.3 of this manual for details.

AS   Alarm System

AS [1 to 19], Alarm Relay 1/0, Dial Out 1/0

AS 	           Displays the system alarm table summary.

AS [1..19]     Displays the individual system alarm

AS [1..19],!  Turns OFF system alarm. Use AS [1..19],1 or AS [1..19],,1 to enable.

[ 1]   AC Power Outage 		More than 1 Hour

[ 2]   Checksum Failure   Reset Setpoints

[ 3]   Feed Pump time     limit exceeded

[ 4] Variable Cycles OFF  invalid control eqn.

[ 5]   Feed Verify OFF,   check FV set-up

[ 6]  Feed Pump failure   feed verify trips

[ 7] Conductivity Sensor  No.1 Open

[ 8] Conductivity Sensor  No.2 Open

[ 9]  12V Power Shorted   Wiring Fault

[10]   Boiler Blowdown    Fail To Sample

[11]   Boiler Blowdown    Flashing

[12]    Corrosion Rate    No-Sensor Fault

[13]    Corrosion Rate    Overrange Fault

[14]    Corrosion Rate    Pitting Alarm

[15]    Corrosion Rate    Conductivity Fault

[16]  Network Controller  Not Responding

[17]  Network Controller  Checksum Failure

[18]  Network Controller  Unexpected Response

[19]  Network Controller  Is In Alarmed State

BL   BoiLer Blowdown

BL[Relay 1..8] [Sample Time],[Wait to Measure],[Blowdown],[Wait to Sample], [Status U..Z]

Secs                    Secs                    Secs           Minutes

where Status is optional

The BL command is only active for Relays having BL in their SWitch command Special Control.

Boiler Blowdown Control Sequence

| Step | Action | Notes |
| --- | --- | --- |
| 1. | Sample, open valve to obtain fresh boiler water sample. | Typically set for 30 seconds. |
| 2. | Wait to Measure, allows valve to close and finite sample cooling to occur. If conductivity < setpoint then goto 4 If conductivity > setpoint then goto 3 | Typically set for 60 seconds. |
| 3. | Blowdown, valve open time if conductivity above setpoint. | Typically 120 - 360 seconds. |
| 4. | Re-Sample, time between samples in minutes. | Anywhere from 10 to 900 minutes depending on boiler size & load. |

Forcing a Control Update

Anytime any of the components of a BL command are changed the controller starts a new Sample 					period. For a bleed valve on Relay #5, a new sample occurs after the BL5,31 command if the previous 				sample time was 30 seconds.

Clear Alarms? on the LCD or the CA$ serial command starts a new sample sequence.

Status [ U..Z]	Fail-to-Sample System Alarm

BL monitors the state of the optional Status thermal switch input	to verify that the thermal switch is 					closed at the start of every Wait to Measure & Wait to Sample interval. If the Status thermal switch 					is not closed, System Alarm AS10 is set equal to the Switch#.

BY   Good-BYe

BY: Bye, ends serial or modem session

Modem terminates automatically on carrier detect drop-out

Serial connect prompts for password  on ENTER.

BY is executed automatically by the controller after two hours without a keystroke on modem 								communications only, re-activating the local  LCD display.

CA    Clear Alarms

CA [ Parameter A..Z ]     Clear designated parameter alarm

CA [Relay# 1..8]              Clear Time owed, Time This Actuation and Time Today on Relay

CA! 						  	Reset all Parameter Alarms  A thru Z

CA$ 							Clear Time owed, Time This Actuation and Time Today on Relays 1 thru 8.

CA*                                   Clear All Active System Alarms

CC    Current  Control

CC [Loop# 1..4], [Relay# 1..5 of Parameter A..J ], 4mA Level, 20mA Level

Connect a Parameter or Relay Control Equation to a current loop and set the 												4mA level and 20mA level for the current loop.

CC@				               Displays all four 4 & 20mA levels, present value of Parameter  & Loop Current

CC [ 1..4 ]				  	Displays selected loop parameters.

Example1:  CC2,C, 8.05, 10.2

Typical ACID feed command, Sets Current Loop#2 to 4mA @ pH=8.05 and 20mA @pH=10.2

Current loop #2 drives variable speed acid feed pump controlled by electrode 												connected to input ‘C’

Example2:  CC1,C, 11.4,  8.3

Typical CAUSTIC feed command, Sets Current Loop#1 to 4mA @ pH=11.4

and 20mA @pH=8.3.

Current loop #1 drives variable speed caustic feed pump controlled by 														electrode connected to input ‘C’.

SELECTING A SOURCE

Any parameter A thru J or the result of any Relay 1 thru 8  control equation may drive a 4-20mA 						current loop. D/A#1 to D/A#4

CONTROLLING CHEMICALS

Current Loop chemical control is inherently PI, Proportional, Integral with the Proportional set by the 					CC command and the Integral fixed by the A/D reading rate, typically updated every 13 seconds.

RESOLUTION

Current Loop resolution is typically 0.5% of full scale. The D/A drive level is 8 bit, with the Drive level 					shown on the CC@ display as a number from 0 to 255.

When connecting to a DCS (Distributed control system) set the 4 & 20 mA levels to reflect the 							expected change in the monitored parameter to limit resolution problems.

For example, monitoring a conductivity which is normally 2,000uS  with a 4mA level = 1500 and a 						20mA level = 2500 gives an excellent 4uS resolution.  Using 4mA = 0uS & 20mA = 10,000uS

results in a lower 40uS resolution.

###### INTERLOCKING, ALARMS & TIME-OUTS

A variable speed pump may be 120VAC powered by a controller relay. See the EN special control under the SW command.

CD    Corrosion Display

CD      Start Corrosion Display, from 1 to 4 Corrosion Rate sensors may be displayed.

Enter  End Corrosion Display

Requires Controller Option SAT-CR or SFT-CR

#     Descriptor                Anodic      Cathodic     Pitting        Rate        Alloy       State

(uA)             (uA)            (uA)       (mpy)       #

G    Tower Corrosion       +1.940        -1.860          0.06             1.56       1.000   Read Pitting

I     Closed Loop               +0.860        -0.840          0.69             0.93       1.000   First Synch

M    Process Corrosion    +10.74        -12.26          3.28              6.45       1.000   Read Anodic

Use the PA command to change descriptors.

Refer to the Corrosion Rate Sensor manual appended to the user manual for application information.

CK    Clock, Date & Time

CK WEEKDAY,  MONTH,  DAY,YEAR, HOUR, MINUTE, SECOND

Example:  CK TUE,  01, 12, 97, 18, 15, 00

Sets the clock to Tuesday, Jan 12,1997  6:15 PM

CK  Displays the current time & date.

WARNING:  Changing the clock alters the stored data time stamp and

erases all stored data.  Execute the CK command on commissioning only

CL   CaLibrate

CL [ Parameter A..N ]

OPTIONS: Use the LCD for single point calibration of conductivity, pH and temperature or use the PA command and directly modify GAIN or OFFSET

CL Automatically calculates OFFSET & GAIN on the selected parameter using the following sequence.

The controller will prompt you through the two point calibration process & allow you to accept or reject 					the calculated values at the end of the process.

Any two operating points, in any sequence may be used for calibration.

Generally, the farther apart the operating points, the more accurate the resulting calibration.

Calibration Sequence:

| Step | Action | Notes |
| --- | --- | --- |
| 1. | Place sensor in first position & press ENTER | pH electrodes in 4 or 7 buffer Conductivity electrodes in air ( 0 uS) Level Sensors in air ( 0 Gallons) Thermal sensors in a cup of ice cubes & water. |
| 2. | Enter first value in sensor units. | 4.0 or 7.0 for pH 0 for conductivity 0 for level sensors 32 for thermal sensors. |
| 3. | Place sensor in second position & press ENTER. | Install pH, conductivity, level & thermal sensors in the target system and use the actual operating level as the second calibration point. |
| 4. | Enter the second value for the sensor | Typically 8.24 for pH, 2352 for conductivity, 106.5 for level and 81.6 for temperature sensors. |

Example ‘CLJ’ : A liquid level sensor in a  55 gallon drum 	filled with 46 gallons of inhibitor, 														connected to the ‘J’ input.

| Step | Prompt | Action |
| --- | --- | --- |
| 1. | Place sensor in first position then press ENTER | Pull the level sensor out of the drum & place it beside the drum then press Enter. |
| 2. | Enter the value of the position. | Type 0 then Enter |
| 3. | Place sensor in second position then press ENTER. | Re-install the level sensor in the drum & press Enter. |
| 4. | Enter the value of the position. | Type 46 then enter |
| 5. | OFFSET = 16.75 GAIN= 13.19 Keep these values? (Y/N) | Select Y or N and Calibration Completed |

CP      Change Password

CP [ 1,2 or 3 ]

CP1    Configure Level,   Up to eight alphanumeric characters, excluding commas.

CP2    Operator Level,    Six numeric digits to allow keypad entry

CP3    Observer Level,   Three numeric digits to allow keypad entry

WARNING

- Record passwords in a secure location. Use the PW command to view passwords for Level 1-3.

2.   LCD Operator Level access is denied by using a CP2 password with alpha characters.

Use this method to lock out local access to setpoint adjustment.

CR      Conductivity Range

CR[E or F] [ 1,2,3,4 ]

CR    Displays the current drive levels for Parameters E & F

Conductivity Range sets millivolt the drive level for the conductivity sensors connected to

Parameter E & F inputs.  CR defaults to 100mV on start-up.

Where 1 = 50mV,  2 = 100mV, 3 = 150mV, 4 = 200mV

CR is set once to match the controller to the sensor and application.

Controllers configured to drive boiler blowdown sensors will be set to Level 1, 50mV on power-up

Controllers configured to low conductivity sensors will be set to Level 4, 200mV on power-up.	4.2.3

CU      Current State

CU [ Parameter A...Z ]  or  CU [ Relay 1..8 ]

CU [ Parameter A...Z ]

Displays the current state of a Parameter in eight lines.

Parameter [Parameter Letter] : [ Descriptor ]

Current Value: [ Value ] [ Units ]   Offset: [ Value ]    Gain: [ Value ]

Raw AD Value: [ Value before conditioning ]

Five minute average: [ Value ]  Last Hour Average: [ Value ]

High Alarm: [ Value ]     Low Alarm: [ Value ]

Delay: [ Minutes from fault to Alarm ]  Timer: [ Minutes Alarmed ]

Relay Alarm: [ YES/NO ]   Dial Out: [ YES/NO ]

Used in switch equations: : [ List of Relays using this parameter ]

CU [ Relay 1..8 ]

Displays the current state of a Parameter in two lines.

Parameter [Relay Number] : [ Descriptor ]

Current state : [ ON/OFF ]   On Time: [ Minutes Today ]   Time Owed: : [ Minutes ]

The CU command	is very useful for users with custom controllers with unusual compensation 							algorithms.

DA      DAta Download

DA [ A, D, W, M, H, T ]

A  =  ALL,      	35 days of hourly data.

D  = DAY,      	Last 24 hours, midnite to midnite of hourly data.

W = WEEK   	Last week SUN midnite to SUN midnite.

M = MONTH 	Last calendar month, or applicable fraction of a month from 6  to  28-31 days of 											hourly data

H  = HOURS		Last two hours of five minute data.

T  =  TODAY     Hourly data from midnite of current day.

DA: FILE FORMAT, ASCII text comma delimited, 71 lines per file.

The first line of the data file consists of the first three parameters of the SS command

Owner, Equipment, Download Filename

The second line of the file defines the frequency of the data.

DAT  			2nd line:  Hourly from, [ Date ] , [ Time ]

DAH  			2nd line:  Every 5 minutes from, [ Date ] , [ Time ]

DAA,D,M,W 2bd line:  Hourly from, [ Date ] , [ Time ]

The third line of the data file lists then one letter names of all 34 parameters and switches, comma 							delimited

Lines 4 through 37 of the data file each consist of a single parameter or relay data, comma 									delimited, oldest data first, most recent data last with the frequency defined by line 2.

Lines 38 through 71 lines of data file are parameter and switch descriptors, one per line.

MISSING DATA:  If the controller has been turned OFF, asterisks will be sent in place

of data to prevent confusion with zero which could be valid data.

UNUSED PARAMETERS:  All 34 parameters are transmitted in response to every command to 												simplify parsing, data storage and controller upgrades.  Unused sensors, 													inputs relays.. are sent as comma delimited asterisks.

DI      DIagnostic

DI	Displays

Controller type:				 [ SMART-FLEX or AS]

Software Version:			 [ Version# ]

Watchdog Resets:			 [ Number ]			     Note 1

Reference Voltage:			 [ Value ]					Note 2

12 Volts DC: 				 [ Value ]					Note 3

Default Configuration: 		 [ Number & Name ]	Note 4

Network Protocol:			 FlexNET  [ Master or Slave ]           Option ‘NT’

Installed Options:										Note 5

Serial Port  								Option ‘R2’

Modem Communications               Option ‘RM’

Alarm Relay                                     Option ‘AR’ or ‘AD’

RS485 network                                Option ‘NT’, FlexNET

D/A Output Driver                           Option IC, IP and/or IO

Feed Verify								Parts: SFX-FV, SFX-FV2 & SFX-FL

Active relays:  1,2,3,4,5,6,7,8							Note 6

Testing Modem: [ Check for modem connected ]

DIAGNOSTIC NOTES

1. Multiple Watchdog resets indicate an electrically noisy site location. Move the controller or install in a 							metal enclosure and ground the enclosure.

2. Flex Only: The Reference Voltage is always 1235.0 +/-10.

This voltage level controls the A/.D converter accuracy.

3. This level will be 1100 +/-100 unless the 12VDC external supply used for water meters and level 								sensors is shorted. A level of less than 900 indicates wiring problems with the 12VDC supply.

The external 12VDC supply is thermally fused so that shorting the supply will not shut down 							the controller.  Clear the short immediately of circuit board damage will occur.

4. The default configuration is loaded when the SD (Set Default) command is executed.

This is the ‘As Shipped’ configuration.

5. Options included when the controller was purchased and shipped.

6. Relays turned ON by the manufacturer. Relays that are not turned ON cannot be

Enabled or used for pump or valve control.

DO      Dial Out

DO [Wait time] , [phone#1] , [ tries ], [phone#2] , [ tries] , [ phone#3] ,[ tries],pager message

DO Displays syntax and current settings.

Wait time :  [ Time between tries in seconds with minimum <= 30 to allow for incoming calls ].

Phone #1 : [ Phone# with area code & outside line digits if required. A Period  = 2 sec. delay]

Tries 		 :  [ 0 - 99,  ‘0’ tries bypasses the phone# ].

Pager Message:  [ Numeric string 1 to 6 digits to identify site ]

Must be numbers only to prevent modem conflict

PAGERS

phone#3 may be a pager of a third modem.

If tries > 0 then after a connect delay set by the number of periods after the phone number,

the pager message is sent to the pager.

Pager dial-out requires setting the pager option with the SS command. You may require several trials 				will differing number of periods to get the delay required to work with your particular pager.

PAGENET typically takes 6 periods to post pager message successfully.

Dial Out on Alarm requires either a pager AQUATRACKER software running on the receiving PC.

After a connection with the remote PC, the controller sends SITE#, Time & Date & then hangs up.

The controller executes one successful transmission of an alarm to all three phone numbers in 						sequence.

WARNING: A dial out alarm will place a phone call every hour until the alarm is cleared.

You or your customer’s communications vendor may charge even for uncompleted calls.

Keep the number of tries to a minimum and respond promptly to alarms.

DR      Display Resolution

DR [ Parameter A..Z or Relay 1..8 ], [ Digit after decimal 0,1,2,3 ]

The DR command is used to set the LCD display resolution.

All other numerical data is transmitted with three digits after the decimal point.

EN      ENable

EN [ Parameter A..Z or  Relay 1..8 ]

Reverses the effect of the EO, Enable Off command

The EN@ command displays which parameters are currently ENabled & Disabled

Enabling a parameter A to N sets the Gain = 1 only if the current Gain=0.

This feature allows the user turn ON unused inputs and then to calibrate using Trackster without effecting 	sensors which are temporarily disabled.

EO      Enable  Off

EO [ Parameter A..Z or  Switch 1..8 ]

Use EO to remove parameters from the LCD display and alarm response.

The EO@ command displays which parameters are currently Enabled & Disabled.

Disabling a parameter or relay shortens LCD scrolling displays

and maximizes software operating speed & command response time.

Any Parameter used in a control equation, interlock or thermal compensation CANNOT be disabled.

Edit the control equation using the SW 	command using ‘!’ to remove reference to the parameter.

FV     Feed Verification

FV[ Relay 1..8 ],[ FV Meter O…T], [Tank Level Parameter G…N], [ppm Parameter G…N],

[C(fixed cycles)  OR  Bleed Relay#1..8  OR  Bleed Water Meter O…T]

FV 				     Without parameters, displays command syntax

FV [ Relay 1..8 ]    Displays current Feed Verification settings on the feed control relay#

[Tank Level Parameter G…N]  Optional – displays and logs calculated tank level, updated very 10mL 										of product pumped.  Sets ‘I’, Inventory parameter compensation.

[ppm, Parameter G…N]  Optional – displays and logs calculated ppm based on gallons from 										midnight and make-up volume, corrected for cycles of concentration.

Blocked on relays not controlled by water meters.

Sets ‘D’, Derived parameter compensation.

ppm calculations require that you define the method for cycles of concentration

applicable only for relays controlled by water meters.

There are three options to set the cycles of concentration

[ C(fixed cycles) ]			Fixed cycles ‘C4.5’ would define a tower where the cycles = 4.5 & don’t vary.

[ Bleed Relay#1..8 ]		If you are controlling based on the ratio of tower to make-up conductivity than 												the Bleed relay control may be used to dynamically set cycles.

[ Bleed Water Meter O…T ]	If you have a bleed water meter than the ratio of Make-up to Bleed volume 												is the current operating cycles of concentration and may be used for 													ppm calculations.

Operating Rules for Feed Verification

1. The FV special control must be set in the feed relay control before using the FV command

2. A maximum of four FV special controls are allowed per Flex & two per ‘AS’ controller.

3. See Manual Section 5.5 for application details.

NS      Network Setup

NS [ !, F, N ] , [ !, U, R, D, M, A ]

Refer to FlexNET manual Appendix R2, for detailed instructions on using the Network Setup command

You’ll have the FlexNET manual appended to this manual if your controller has the NT option.

Summary of NS Command Syntax

NS!      	Turn off all Networking

NSF      	Turn on Networking & select FlexNET protocol. Requires NT option in controller

NSN		Unused, reserved for future RS485 protocols

NS,!        Disconnect a Master controller from the NET.

NS,U       Unassign a slave controller address. NS,U@ unassigns all slaves

NS,R		Register a new slave. Only one slave may await registration at any one time.

NS,D		Disconnect a slave controller but don’t re-assign its address. Used for Service outages.

NS,M  	Make the current controller the Master. Only one Master allowed per net!

NS,A		Assign a new address to a Slave awaiting registration.

NT      NeTwork

###### NT [ Node # where #=@, 1…15 ]

Refer to FlexNET manual Appendix R2, for detailed instructions on using the NeTwork command

You’ll have the FlexNET manual appended to this manual if your controller has the NT option.

Summary of NT Command Syntax

NT{1..15]  	Connects to the designates Slave# 1 to 15 & prompts for the Slave password.

Error messages tell you if the slave exists and if you have connection timeout.

When you are connected to a Slave the command cursor changes from > to [x}>

Where x = Slave Controller#.

Use the BY command to disconnect from the Slave & return to the Master.

NS@     	     Lists all Slaves and their NET addresses.

PA      PArameter

PA [Parameter A..N] , Descriptor, Gain , Offset , Units, Compensation

PA [Parameter O..T] , Descriptor, Gain , Scale , Units

PA [Parameter U..Z] ,  Descriptor     Parameters U..Z are status contacts and therefore can have 																			Descriptors only.

PA [ Relay 1..8 ] ,  Descriptor 		   Relays 1 to 8 can have Descriptors only.

Descriptor   is limited to 20 characters, excluding commas to fit the LCD display

Longer descriptors are truncated to 20 characters.

Gain & Offset are usually set by the CL calibrate function, although these values can be entered 										manually using the PA command.  The displayed value of a parameter,

= Gain x [measured millivolts]  + Offset     (Offset can be ‘+’ or ‘-’ )

Note that Gain is applied before Offset, so Offset must be in user units.

Watermeters ‘O’ through ‘T’

Gain is the numbers of gallons/contact and may be a non-integer equivalent to the ‘K’

Input when the TV Remote is used to calibrate a water meter.

Scale is an integer <255 and is used to divide pulse streams for turbines &

paddlewheels.

Examples:

A contact head water meter at 50 gallons/contact closure connected to input ‘O’

PAO, Tower Make-up, 50,0,Gal                Note that Scale is zero for contact head.

An insertion paddlewheel with 30.8 pulses per gallon noted on the sensor body & 					connected to input ‘Q’

PAQ, Chilled Make-up, 5, 154,Gal            Note that Scale is less than 255.

(Every 154 paddlewheel pulses, 5 gallons of chilled water make-up occurs)

Units  are limited to three letters. For parameters A & B units must be either capital C or F

since Units is used to determine the zero point for temperature compensation.

Compensation:

Blank				=   no compensation applied to the sensor.

T[A..N](%/F)        =  Temperature compensation source and %/ degree C from 20C

For example TA	.97, subtracts parameter ‘A’ value from 70F & corrects the 													current parameter by 0.97%/F

Example:  PAC, 0.02 , 7 ,Cooling Water pH, TM0.02

On the signal from ‘C’; apply a gain of 0.02 x raw millivolts then add 7 then 	temperature correct 						using the temperature measured at ‘M’ at 0.02%/unit

Label this parameter ‘Cooling Water pH’ in all reports and alarms.

###### Using Compensation to Set Corrosion Rate measurements

Requires Controller Option SAT-CR or SFT-CR

CR[E..N] / [Alloy]    = [E..N] is optional and designates the conductivity parameter letter used to

compensate the Linear Polarization measurement.

[Alloy]  is optional and designates the corrosion ratio of the sensor metallurgy

to carbon steel. The default = 1, carbon steel.

Example: PAK, Corrosion rate,,,mpy,CRE/1 would connect a corrosion

Rate sensor to input ‘K’, set the unit to mpy, use parameter ‘E’ for conductivity

compensation and set the alloy = 1 = carbon steel.

###### Using Compensation to Rate-to-Volume Conversion

R[ M or H ]  [Water Meter O…T  ]

‘R’ sets the rate-to-volume conversion used for make and bleed rates in GPM or steam 								production in LB/HR    - See application note AN010-05 for details

M defines a rate in GPM or any rate per Minute

H defines a rate in LB/Hour or any rate per Hour

[Water Meter O…T  ]     defines the water meter for the volume measurement.

Any unused and enabled water meter may be used.

The water meter volume may then be used for pump control.

Do not connect an actual water meter into a water meter input used for rate-to-volume.

Calibrate the water meter for 100 Gallons/contact.

###### Alarm on No Flow – Inputs U to Z Only

PA[ U…Z ]     Displays the current Alarm on No Flow setting

PA[ U…Z ],,1 Sets alarm on no flow on Status switch input U through Z

PA[ U…Z ],,0 Removes alarm on no flow on Status switch input U through Z

Set alarm time to define the interval between contact sets opening and the alarm occurring.

Factory default sets alarm on no flow at five minutes without flow.

Alarm times >1440 prevent alarm on no flow.

PR      PRime

PR@		 Turn ON all Relays for 300 Secs. Relays will not turn ON if Alarmed or interlocked by Status 									Switches or other relays.  The 300 seconds is added to the Timed Owed counter

& will be provided when the interlocks and alarms are cleared.

PR [ Relay 1..8 ], [ Relay 1..8],...    Turn ON designated relay or relays for 300 Secs

Adds 300 seconds to pump time immediately. Does not override interlocks on either Status 									Switches or other Relays.

Use CA$ to clear priming from all relays or CA [ 1..8 ] to clear priming from a specific relay.

The CA command clears all times accumulated today for the target relay.

PW      PassWord

PW 		 Display Passwords for Level 1,2 and 3 access.  Only available at Level 1.

Response

Controller Passwords

Level 3, Observer     [ 333 ]		        Factory default or the current value

Level 2, Service        [ 994466        ]	   Passwords are not case sensitive.

Level 3, Configure    [ pungent$     ]    Any keyboard character or number may be used.

Factory default passwords are supplied on a removable sticker inside the controller enclosure

Controllers with the R2 & RM options may use the CP (Change Password ) command.

RE      REad Continuous

RE [ Parameter A..Z ]   Displays a new line every time A/D data updated with descriptor and value.

Enter key terminates display

RE@A   Analog:	Displays all enabled analog inputs, A thru N, the Reference & 12VDC levels.

RE@F   Flows:		Displays all enabled water meter inputs

RE@S   Status:		Displays all enabled status. contact closure inputs

RE@R   Relay:		Displays all enabled active relay outputs

Enter key terminates display

Display updates with every new set of A/D converter data; about every 14 seconds for Flex series 					controllers and every 7 seconds for AS series controllers.

SD      Set Defaults

SD

Reloads all default descriptors, gains, offsets and control equations from EPROM.

The SD command requires confirmation prior to implementation.

Users are prompted “SD destroys all site configuration data! Proceed Y/N?”

Execute this command only when you wish to return to Factory settings.

The default configuration shown by the DI, Diagnostic command will be implemented.

SO      Site Options

SO  Daylight Savings [1/0] , LCD Scroll Alarms [1/0]

1 turns a feature ON, 0 turns it OFF

The modem initialization string is displayed in response to this command.

Both of these features can be turned ON/OFF using  the LCD & remote keypad.

SS      Site Setup

SS  Site Name, Site Description, Site File ID, Modem Ring Count, Pager Enable [1/0]

SS without parameters displays

Owner Name		  	:  [Site Name ]				Maximum 20 characters, no commas

Equipment Name	  	:  [ Description ]			Maximum 20 characters, no commas

Download File Name	:  [ Site File ID ]				4 Letter, used to identify file on alarm reports,

Ring Count				:  [	Modem Rings 0-12]   Rings before modem pick-up, usually Set=1

Pager						:  [	ON/OFF ]	               Pager =1 to transmit site identifier# from DO command

ST      STatus

ST [Relay 1..8],  [Relay 1..8], [ Parameter A..Z ], [ Parameter A..Z], [ Parameter A..Z]

, [ Parameter A..Z]    Display any two relays & up to four unrelated parameters 																						continuously in real time.

Example: ST 1,2,A,C,   Display continuously switches 1 & 2 and parameters A & C

Refreshing screen whenever any data changes

The ST command is the primary view of controller operation. Control levels, alarms, timers and control 					sequences and equations are displayed on the STatus screens.

Display response to ST3,5 command with bold, italic text indicating variable data.

STATUS              Aquatrac Instruments                    			Date: 12/11/96

SMARTFlex Controller                    			Time: 15:25:30

Acid Pump      Reversed 	Turn ON @	8.00        			Interlock Status

State ON                     		Turn OFF@		10.00           		Operating

Time This Actuation  Control Equation: C     = 6.898   		ALARMED

34.8 Minutes                                         				Switch Interlock

Operating Time Today

37.4 Minutes                                         				Special Control

Operating Time Owed

0.0 Minutes

Boiler Test       	            	Turn ON @		10.00           		Interlock Status

State ON              	       	Turn OFF@		7.00        			Operating

Time This Actuation  Control Equation: C     = 6.898

0.1 Minutes     				                                    Switch Interlock

Operating Time Today

466.4 Minutes                                         			Special Control

Operating Time Owed                                         				Stage: Sample

5.0 Minutes                                             				15 Sec.

SW      Switch

SW Switch commands control the 120VAC power switching relays.

Two Syntax’s are permissible:

SW [Relay 1..8], [Control Equation], [Turn ON[,[ Turn OFF], [Special Control],

[Status Interlock U..Z] , [Relay Interlock 1..8], [R(everse)]

and

SW [ Relay 1..8], [O..T], [Pump Volume ] ,[ Pump Time ], [Special Control],

[Status Interlock U..Z ],[ Relay Interlock 1..8]

For control equations derived from water meter inputs O thru T

Deleting Switch Components

Putting an !, exclamation point between commas deletes the command component

Example:	SW7, , , , ,U   Requires Status Switch ‘U’ to be closed to operate Relay No.7

SW7, , , , ,!    Removes all Status Switches from Relay No.7’s control equation.

SW7, , , , !    Removes all Special Controls including ‘VC’ & ‘FV’ from Relay No.7

Control Equation is:

A parameter  A thru T OR The sum, product or difference of any two or more parameters.

Control equations may include one or more of the following operators

+     Sum of  flows or levels

-      Difference of flows or levels

/      Ratio of conductivities or levels

:      Feed Verification only, pump a user selected mL of product

Examples:

A:    Conductivity control, with bleed solenoid connected to Switch #6 and using a sensor 										connected to ‘E’ input. Bleed if only flow switch connected to ‘U’ is closed.

SW  6 , E,   2000, 1990, ,  U

B:    Chemical pump timing based on make-up from R make-up water meter; 30 seconds for 									every 100 Gallons  if ‘X’ is closed & Relays 1, 2 and 4 are open

SW  5, R, 100, 30 ,, X+Y, 1+2+4

Status Interlock must be closed to enable the relay.

Used for flowswitches and permissive contact sets,. Status switches may be ANDED

by entering U+X requiring both status switches U AND X to be CLOSED to allow the switch to 							operate.  Status switches from U thru Z allowed.

Relay Interlock  must be OFF to enable the Switch.

Used to inhibit feed on bleed or to prevent chemical mixing. Relays may be ANDED

by entering 3+4+6 requiring relays  3 AND 4 AND 6 to be OFF to allow the pump to	 									operate.  Relays from 1 thru 8 allowed.

SW      Switch       cont.

.

# Special Controls:  One of  BF BL BT EN FV HT LO PB PT TC TE TM VC

Where special control is: NO TEXT, for no action

OR

BF[ Bleed Relay# ]		Bleed& Feed Inhibitor Control

Applies ONLY to Relays with water meter control equations.

Overrides the water meter when present in the SW equation

Turns ON the Originating Feed relay whenever the Destination Bleed relay turns ON

Allows the Originating Feed & Destination Bleed relays to have separate	ALARM time-outs

OR

BL				  				Boiler Blowdown Sampling Control

WARNING The BL control enters default boiler blowdown sampling control as soon as the SWitch 							command is entered.  Type BL [ 1..8 ] immediately after the SW command to edit the 									sampling timing. Refer to BL command.

OR

BT[ Bleed Relay# ]      	Bleed Then Feed Inhibitor Control

Applies ONLY to Relays with water meter control equations.

Overrides the water meter when present in the SW equation

Adds the ACTUATION TIME from the Destination Bleed relay to the Originating  Feed relay 									whenever the Destination Bleed relay turns OFF.

Allows the originating feed & destination bleed relays to have separate ALARM	time-outs

OR

EN			  ENable a relay between Setpoints

Turns a relay ON between the [Turn ON] and [ Turn OFF] setpoints	. ENable is a very different relay operation from a deadband which provides control hysteresis to keep a relay, pump or valve from rapidly switching ON & OFF.

ENable will be most frequently used with variable speed pumps and controllers with the IC, IP and/or IO 4-20mA output option.

Plugging a variable speed pump into an ENable controlled power relay allows the use of Status & Relay interlocks as well as ALarm command timeouts

OR

# FV								Feed Verification

Requires FV option in controller – see DI command.

Requires FV command for set-up – see FV command.

Provides ppm calculation,. Fail-to-feed alarm, tank level calculation.

Allows the O:Q control equation to feed a user set mL on ‘Q’ for every user set gallons 		 measured on ‘O’ for relays controlled by Water Meters.

OR

HT[ Hours ]  		           Holding Time

Allows a control equation, which measures the ratio of conductivities to use the raw 										water conductivity averaged over HT hours.

Use HT to prevent scaling during the period after the raw water conductivity falls, while the 								tower water is a mix of mostly high conductivity and some low conductivity raw water.

WARNING: Cycle controllers can only be used when scaling components of the raw 											                           water  track with the raw water conductivity.

HT is not supported via the LCD. Data Logging is required to verify effective cycle 										control over the HT period, restricting the HT function to controllers with R2 & RM options.

Sample Cycle Control SW Command:

SW2, E/F, 4 , 3.9,  HT20

Control relay #2 on the ratio of the of conductivity sensors connected to E and F inputs.

E = Tower Conductivity  F = Raw Water Conductivity.

Average the value of F over 20 hours.

Use the ST1,2,E,F command to view the action of the control equation in real time.

You’ll see the value of the E/F control equation change immediately when the value of tower 							water conductivity ‘E’ changes.  The value of the control equation will not change when the 								the value of raw water conductivity ‘F’ changes.  Every hour the average value of ‘F’ over 								the Holding Time is recalculated. So if the HT value is short and the change in F is large, 								you’ll see a change in E/F on the hour.

.					OR

LO [ Destination Relay# 1..8] / [ Time in Minutes]		Lockout Bleed Relay on Chemical Feed

Prevents the Destination, Bleed relay from turning on for the selected minutes every time a 								timed event occurs on the Biocide Feed relay.

Lock-out is used to prevent blowdown during biocide reaction times.

Example:

Every two days biocide is added using the pump connected to Relay 7.

Tower blowdown uses Relay 2

SW7, , , , LO2/180    Locks out Bleed Relay #2 for three hours every time a TE event 																occurs on Relay #5

OR

PB[ Destination Relay# ] / Minutes 		Prebleed on Biocide Feed

Prebleed adds an event of Minutes to the destination prebleed relay TE Timed Events 									whenever an event is added to the originating relay’s TE Timed Event table.

Prebleed is only set ONCE for each relay. It’s either ON or OFF

OR

PT [ Seconds]		  		Percentage Time Inhibitor Control or Chemical Feed

Sets the number of seconds in every five minutes that the relay is ON.

The selected number of seconds is added at the beginning of every five minute period to 								permit both verification and predictability.

Seconds shows on the ST screen as  Time Owed at the start of every five minutes.

OR

TC [ PERIOD in Minutes ] / [ ON time in minutes ]           Timed Cycling

Duty cycles a relay ON/OFF for a user defined ON time in every user defined PERIOD whenever the controlling sensor is between the Turn ON & Turn OFF setpoints. Fully detailed in Section 5.8 of this manual.

OR

TE	       		Timed Event Interlock for ‘Slug-til-it-ORPs Biocide Control’

Used at sites where the control equation is active for only limited periods each day.

This active time will be set using the TE command to select times and setting TE under 									Special Control in the SWitch equation.

Timed Event will shows up under Special Control on the ST screen.

Example:

Two hours every day the ORP in the cooling water is raised to 300mV with the hypochlorite 		pump connected to Relay 5 & the ORP electrode connected to parameter ‘C’, interlocked 		with flowswitch connected to ‘U’

SW5,  C, 300, 290, TE, U    Enables the control equation based on Timed Events

TE5,1,12:00,120                  Sets the times that the control is active.

OR

TM [ PERIOD in Seconds ]           Time Modulation

Duty cycles a relay ON/OFF proportionate to the dead band between the controlling sensor Turn ON & Turn OFF setpoints.

User can set 100% ON time at Turn ON or at Turn OFF by using the Reverse field of the SWitch command.  Minimum and default PERIOD = 60 seconds

For example, you can have the Bleed valve ON for 1 second in every 60 seconds at the turn OFF setpoint. %ON time increases linearly as the conductivity increases to the Turn ON setpoint where the valve is ON for 60 seconds in every 60 seconds.

Fully detailed in Section 5.7 of this manual.

OR

VC	       		Variable Cycles

Requires VC command for set-up – see VC command.

Provides three make-up conductivity ranges and user set cycles for each range.

User set maximum tower conductivity.

R(everse)     		 Reverse the Turn ON, Turn OFF sequence

Requires |Turn ON level| < |Turn OFF level|. Without ‘R’, this inequality would cause a syntax 							error. The ‘R’ designation allows intentional reverse switch logic.

R(everse) is used to add caustic on pH control and to open bleed valves on low conductivity.

In both of these Reversed modes, the switch is ON when the when the Control Equation is 								less than Turn ON and OFF when the Equation is greater than Turn OFF

Examples A & B:

A:  Caustic control, with pump connected to Switch #5 and using a pH sensor connected to 										‘D’ input. Pump if flow switch connected to ‘X’ is closed and Switch 6 (Bleed) is OFF

SW  5 , D,   8.5, 9.2,  ,  X, 6 , R

Switch ‘5’ ON when ‘D’ < 8.5 and OFF when ‘D’ > 9.2

B:  Closed Loop Conductivity control, with inhibitor  connected to Switch #7 and using a 											conductivity sensor connected to ‘F’	input. Feed if flow switch connected to ‘V’ is closed.

SW  7 , F,   800, 750, ,  V, , R

Switch ‘7’ ON when ‘F’ < 800 and OFF when ‘F’ > 750

TE      Timed Events

TE[ Relay 1..8 ],[ Day# ], [ Start Hours: Start Minutes] , [ Duration (min) ]

TE 					Without parameters both syntax and current day#  timing cycle, 7, 14 or 28..

TE@ [ Relay 1..8 ]  Displays events for the specified relay.

TE[ W or M ]  Sets the timing period in days.

W = 7 day cycle,  M = 28 day cycle

TE!					Resets Day#1 to the most recent Sunday.

If today is Sunday than the current Day# is set to 1.

Operating Rules for Timed Events

1. Maximum Number of Events = 28 per relay per period.

2. Duration in minutes settable from 1 to 1439 ( 1 Minute to 24 Hours )

3. Timed events do not carry over into the next day to prevent inadvertent scheduling errors.

4. Removing an event be entering a duration of ‘0’,  zero, minutes.

PREBLEEDING & LOCKOUT

Prebleeding lowers the cooling tower conductivity prior to adding biocide by opening the bleed valve or 				  solenoid.   See SW command for defining which Relay prebleeds or is locked out.

TS     Test

TS   Test pH/ORP and Conductivity Sensors

This test is performed automatically every hour on the hour.

The TS command forces the test to occur now.

Conducts impedance tests on both pH electrodes and checks for fouling on both conductivity electrodes.

Reports:

[C], [ C Descriptor ]    Value,  Test Value    Pass/Fail

[D], [ D Descriptor ]    Value,  Test Value    Pass/Fail

[E], [ E Descriptor ]    Value,  Test Value    Pass/Fail

[F], [ F Descriptor ]     Value,  Test Value    Pass/Fail

UG     UpGrade

UG  [ Upgrade Code ]

Adds controller features using a Code keyed to your serial number

UpGrade is active in controllers with Version 3.00T and later software.

Currently it’s used to view your electronic serial number.

UG & Enter key provides this response

UG  [ Upgrade Code ]  (command syntax)

To upgrade your controller features, contact Aquatrac Instruments with your serial number

SN: [ 57ea3566 ]

VC     Variable Cycles

VC[ Relay 1..8 ],[ Low Make-up uS], [Low Setpoint Cycles] , [ Medium Make-up uS ],

[Medium Setpoint Cycles],  [High Make-up uS], [High Setpoint Cycles],							[Max tower conductivity]

VC 				     Without parameters, displays command syntax

VC [ Relay 1..8 ]    Displays current Variable Cycle settings on the blowdown relay#

Make-up uS           Below each range’s make-up uS, the blowdown controls at that range’s cycles

With a 1% deadband.

Max Tower Conductivity		The blowdown controls with a 1% deadband if the tower conductivity 											exceeds the user set Max Tower Conductivity.

Operating Rules for Variable Cycles

1. The VC special control must be set in the bleed relay control before using the VC command

2. A maximum of four VC special controls are allowed per controller.

3. See Section 5.4  for application details.

WM     WaterMeters

WM     Displays the two years of summary water meter data stored in

the controller EEPROM for all six water meters.

| Water Meter | Descriptor] (Typical Shown) | Units | Today | This Year | Days this Year | Last Year | Days Last Year |
| --- | --- | --- | --- | --- | --- | --- | --- |
| O | Tower1 Make-up | GAL | 6,880 | 1376400 | 186 | 1594781 | 200 |
| P | Tower1 Bleed | GAL | 1,240 | 344100 | 186 | 189740 | 186 |
| Q | No.1 Closed Loop | L | 2 | 624 | 186 | 36 | 200 |
| R | Tower2 Make-up | GAL | 9,460 | 2604000 | 186 | 1456040 | 100 |
| S | Tower2 Bleed | GAL | 2,105 | 667692 | 186 | 394210 | 100 |
| T | No.2 Closed Loop | L | 0 | 0 | 0 | 105 | 85 |

Where Days This Year  & Days Last Year are the number of mid-nites that the controller stored water 				meter data.

XC     Xtra Configure

XC@ [ A, F ,R ,S]	Display the extra configuration option lists for:

Analog Inputs OR Flows OR Relays or Status Switches.

XC Para [Val]      Set the Parameter or relay configuration = value selected from an XC@ option list.

Where Para = A to N, O to T, U to Z or 1 to 8

An XC option defines descriptors, gains, offsets, compensation, alarm levels and timeouts, controls …

Used to simply, quickly and thoroughly re-configure a controller.

#### CUSTOMIZING CONTROLLERS FOR FUTURE USE

XC selections are stored in EEPROM and are loaded on every power ON

even if the memory back-up battery has discharged.

Configure a controller for the end user. Install and commission months later without loss of configuration.

4.3 Data streaming, ‘AP’ commands

The AP command is used by Trackster to acquire condensed, comma delimited data from the controller

The AP command may also be used to support a parser for user interfacing to other automation systems.

AP & ENTER responds with invalid command error message

APTRACKSTER,0 & Enter

Responds with Software Version, always 0.0.1  Supports handling of future data streams.

APTRACKSTER,1  & Enter Responds with the current controller configuration

One line for each enabled I/O , 4-20mA  outputs and corrosion rate always sent.

Data set requested on connection for current controller state

Analog   (Seven lines for AS & fourteen for Flex)

Parameter Letter A-N, name, units, gain , offset, compensation value, compensation parameter, compensation method, high alarm, low alarm, delay on alarm   Newline

# Water Meter (Three lines for AS & six for Flex)

Parameter Letter O-T, name, units, gain , offset, scale,  high alarm, low alarm Newline

# Status Inputs (Four lines for AS & six for Flex)

Parameter Letter U-Z, name, high alarm Newline

# Output Relays (Five lines for AS & Eight for Flex)

# Relay# 1-8, Name, Control equation, on time alarm, day alarm, Turn On Level, Turn OFF level, Pump Volume, Pump Time, Relay Interlock, Status Interlock, Special Control, Special Control Relay Newline

Any relay used for boiler control has a following line:

B Relay#1-8, Sample Time, Wait-to-Measure time, Blowdown Time, Resample Time, Fail-to-Sample Input, Reference Relay Newline

Corrosion Rates (Four lines)

C rate 1-4, Paramater Input A-N, Conductivity Input for compensation, Alloy Number Newline

4-20mA Outputs (One line)

D1, 4mA level, 20mA Level, Controlling sensor, meter or relay

D2, 4mA level, 20mA Level, Controlling sensor, meter or relay

D3, 4mA level, 20mA Level, Controlling sensor, meter or relay

D4, 4mA level, 20mA Level, Controlling sensor, meter or relay

APTRACKSTER,2  & Enter  Responds with the current state of all I/O

One line for each enabled I/O , 4-20mA  outputs and corrosion rate always sent.

Data set sent each time command issued.

Analog   (Seven lines for AS & fourteen for Flex)

Parameter Letter A-N, State, Value, Alarm Timer in seconds, Last Hour average Newline

‘State’ is a byte with bit’s 0..7 set as follows:

| Bit | Decimal Value | Substate |
| --- | --- | --- |
| 0 | 1 | Enabled |
| 1 | 2 | Alarmed |
| 2 | 4 | Alarm Relay |
| 3 | 8 | Dial Out |
| 4 | 16 | Overrange |
| 5 | 32 | Specialized |
| 6 | 64 | Used in a Boiler |
| 7 | 128 | Unused |

# Water Meter (Three lines for AS & six for Flex)

Parameter Letter O-T, State, Value, Total, Last Hour value Newline

‘State’ is a byte with bit’s 0..7 set as follows:

| Bit | Decimal Value | Substate |
| --- | --- | --- |
| 0 | 1 | Enabled |
| 1 | 2 | Alarmed |
| 2 | 4 | Alarm Relay |
| 3 | 8 | Dial Out |
| 4 | 16 | Alarm Override State |
| 5 | 32 | Unused |
| 6 | 64 | Unused |
| 7 | 128 | Unused |

# Status Inputs (Four lines for AS & six for Flex)

Parameter Letter U-Z, State, Total time, Ontime, Last Hour value Newline

State’ is a byte with bit’s 0..7 set as follows:

| Bit | Decimal Value | Substate |
| --- | --- | --- |
| 0 | 1 | Enabled |
| 1 | 2 | Alarmed |
| 2 | 4 | Alarm Relay |
| 3 | 8 | Dial Out |
| 4 | 16 | ON |
| 5 | 32 | Invert Logic |
| 6 | 64 | Unused |
| 7 | 128 | Unused |

# Output Relays (Five lines for AS & Eight for Flex)

# Relay# 1-8, State, Control Value,Special time, Special Wait Time, On time, On Total, On Now,  Last Hour on time Newline

Any relay used for boiler control has a following line:

B Relay#1-8,State, countdown time Newline

Output Relay ‘State’ is a byte with bit’s 0..7 set as follows:

| Bit | Decimal Value | Substate |
| --- | --- | --- |
| 0 | 1 | Enabled |
| 1 | 2 | Alarmed |
| 2 | 4 | Alarm Relay |
| 3 | 8 | Dial Out |
| 4 | 16 | ON |
| 5 | 32 | Reversed |
| 6 | 64 | Interlocked |
| 7 | 128 | OFF an Alarm |

4-20mA Outputs (One line)

D1, Drive1 level 0-255 D2, Drive2 level 0-255 D3, Drive3 level 0-255 D4, Drive4 level 0-255

(Note: no Newline)

Corrosion Rates (Four lines)

C rate 1-4, anodic level, cathodic level, pitting level, rate mpy, state Newline

5. Application Notes

5.1 Enclosure Installation

Typical controller enclosure installation for ‘AS” controllers with the RM option and for all Flex series controllers. Industrial sites may use the larger LE16-14, options with internal terminal blocks and without plug box(es)

5.2 PM Schedule

| Sensor | Cleaning See Note 1 & Caution | Verify - Calibrate | Replacement Schedule |
| --- | --- | --- | --- |
| Conductivity | Whitish or brown deposits: dilute HCL Organic Fouling: alcohol, solvents or soap & water. See Note 3 | Verify monthly Calibrate as needed See Note 2 | 2 years |
| Corrosion Rate | Do not clean Refer to user manual if pitted. | User calibration not required. See Note 4 | 2 years Tips only |
| Flowswitch | Dis-assemble to verify mechanical operation and remove debris. | Valve OFF flow during every system service and verify flowswitch Shows OFF. Perform at least monthly. |  |
| ORP | Whitish or brown deposits: dilute HCL Organic Fouling: alcohol, solvents or soap & water. Failure to track: 5% nitric for 5- 10 minutes. See Note 5 | Verify monthly Do not calibrate. See Note 5 | 1 year |
| pH | Whitish or brown deposits: dilute HCL Organic Fouling: alcohol, solvents or soap & water. See Note 6 | Verify monthly Calibrate as needed See Note 6 | 1 year |

## Caution – Removing Oils, Greases & Biofilms from pH & ORP sensors

## Solvents that will not attack the sensor body are an alternative method to soap & water.

## Methanol and isopropyl alcohol are acceptable solvents.

## Acetone, MEK, THF, or trichloroethane may irreparably harm the sensor.

## A soft toothbrush can be used with the detergent to remove stubborn coatings.

Notes:

Note 1: Do not clean sensors unless there are operational problems: failure to track, calibration out of range, 			mechanical damage.  Excessive cleaning may reduce the operating life of pH sensors.

Single point calibrate pH, ORP & conductivity sensors by sampling the cooling water and keying the				 current conductivity or pH into the controller. There is no increase in control accuracy when sensors are 		two point 	calibrated.

Note 2: Calibrating more frequently than every 30 days indicates operating problems. Systems with effective 			water treatment will operate a year or more between calibrations.

Note 3: Clean with a solvent  before re-calibrating. If conductivity increases, sensor was organically fouled:				 locate the source & correct.

Note 4: Controller system level alarms indicate operating problems. Operating problems which foul 						conductivity sensors will also foul corrosion rate sensors.

Note 5: ORP sensors read +/-5mV of the actual ORP. If sensors are reading high or low or failing to respond 			to 	oxidant, then there is an operating problem which cannot be fixed by calibration.  Operating problems 		which 	foul conductivity sensors will also foul ORP sensors.

Note 6:  Calibrating more frequently than every 30 days indicates operating problems. Reddish or black Iron 			deposits will prematurely fail pH sensors. Dropping or rapping the sensor on a hard surface may micro-			crack the pH sensitive glass and result in a fixed pH, which does not change with acid or caustic					addition.

5.3 Rate-to-Volume Conversion & Control

### 5.3.1 OBJECTIVE

Details converting 4-20ma on Rate to Volume for the ON/OFF control of chemical feed pumps.

### 5.3.2 TYPICAL APPLICATIONS

- Convert a make-up water meter from GPM to Gallons and use the volume to set the ON time of inhibitor pump. For every 250 Gallons of make-up, turn the pump ON for 23 seconds.

- Convert a steam demand meter or meters from lbs/hour to lbs of steam. Use the steam volume to control fractional horsepower amine and boiler treatment pumps. Every 10,000 pounds of steam turn ON the pumps for 46 seconds.

- Convert a production line speed in Feet/per/second at 4-20mA to ON/OFF control of a process chemical.

### 5.3.3 REQUIRED SOFTWARE

Controller software Version 3.52 or later & controller with R2 or RM option.

Trackster Version 2.1 or later with Terminal screen option.

As of 05/01 Trackster does not support the ‘R’ sensor compensation option.

Supporting References:

Loop powered, 4-20mA current loop isolators: www.omega.com   OMEGA part CCT-100, approximately 	$130.00 ea.

# 5.3.4 INSTALLATION

5.3.4.1 Hardware Installation – Connecting the 4-20mA cable,

- Connect the 4-20mA signal to a sensor controller input. Any unused input  G to N on a ‘Flex’ or G to J on an ‘AS’ series controller may be used.

- CAUTION: 4-20mA  signals that are used by other equipment usually require loop isolators to prevent ground loops. Aquatrac’s controllers ground one side of the current loop. A ground loop occurs if the other equipment monitoring the loop also grounds the current loop. If in doubt, install a loop isolator: see Supporting references in Section 5.3.3

- Connect to the controller and verify that the analog input that you intend to use is not being used for Feed Verification ppm or inventory tracking.

- The following example uses analog input ‘J’ & water input ‘Q’.

Prior to terminating the current loop, verify that the LJ jumper is installed ½” inboard from the J controller 		terminals. The factory default has the LJ jumper installed & it will be installed unless you are converting

input ‘J’ from a prior use.

Connect the 4-20mA current loop to J+ and the negative of the loop to J-.

The LJ jumper terminates the current loop with 50 ohms.

Any unused analog input and water meter input can be used for Rate-to-Volume conversion.

5.3.4.2 Software Set-Up –  ‘J’ & ‘Q’ Example

- Connect to the controller using Trackster at the Configure password level and using Diagnostic View II

- Right click on sensor ‘J’ and enable sensor ‘J’

- Right click on meter  ‘Q’ and enable meter ‘Q’ and set its descriptor: Make-up, Steam Production, Line Speed… and units: Gal, Lbs, Ft…. descriptor & Units have no effect on function.

- Set the gallons/count for water meter ‘Q’ for 1 for GPM &  LBH.

- Right click on the inhibitor pump, select Configure Control and key Control-Alt-Shift & you’ll be in the Trackster terminal screen

- Key Enter to get to the command prompt ‘>’

- Key PAJ,,1 & Enter

- Close the terminal window select sensor ‘J’ and calibrate for 4mA and 20mA levels. Use the theoretical 4-20mA calibration, it’s accurate enough to verify you have a functioning current loop.

- Verify the current loop displays correctly on sensor ‘J’. Set the sensor ‘J’ descriptor and units: GPM, LBH, FPM…. descriptor & Units have no effect on function.

- Right click on the inhibitor pump, select Configure Control and key Control-Alt-Shift & you’ll be in the Trackster terminal screen

- Key Enter to get to the command prompt ‘>’

- Key PAJ,,,,,RMQ & Enter for Gallons/Minute or PAJ,,,,,RHQ & Enter for LBs/Hour & close the  terminal window,

- Verify that water meter ‘Q’ updates every 14 seconds: Flex series controllers or 8 seconds for ‘AS series controllers. For example: a Flex series controller with 100 GPM on ‘J’ would add 200 Gallons to meter ‘Q’ every two minutes.

- Water meter input ‘Q’ may be used for control of any pump with Control Equation =’Q’ either by itself or summed with other meters.

5.3.5 TECHNICAL-OPERATIONAL NOTES

- Rate-to-volume conversion occurs when the Rrm command is placed in the sensor compensation field  using the PA command, where R=Rate-to-volume, r= M or H for GPM or LBH respectively & m = water meter input O to T: Flex or O-Q:AS.  M assumes a rate/minute & H a rate/hour.

Keying PAJ  &  Enter will display R 60 Q if rate per minute or R 3600 Q if rate per hour.

- Any unused, enabled input  ‘G’  to ‘N’ and meter ‘O’ to ‘T’ can be used. If you attempt to use a non-enabled water meter, you’ll get the Cannot Compensate on a Disabled Parameter!, error message.

- The water meter input, ‘Q’ in our example, cannot be used for an actual water meter; errors in the gallons/day total will occur.

- Negative rate-to-volume conversions add zero. If you calibrate the 4-20mA loop so that 4mA is, for example, –1 GPM then you ensure that the water meter does not accumulate at 4mA.

- Set the inhibitor pump feed limit timers to prevent overfeeding due to miscalculation or miscalibration of the 4-20mA loop. Ensure that the minutes/per/actuation timer is set high enough to prevent nuisance feed outages.

- Trackster: Rate-to-Volume inputs will display ‘No Compensation’ on the 4-20mA sensor Set Compensation option until Trackster is updated.

- Feed Verification: Rate-to-Volume conversion may be used as the make-up water meter for control of an Inhibitor Pump if the Gain or Gallons/Contact is on the controlling water meter = 1. WARNING: Feed on mL, O:Q type control equations will not totalize correctly unless Gain =1 on Water Meter ‘O’.

If you use ‘XCx’ command to remove relay ‘x’ , you will not be able to re-use the FV control on this relay or another relay until you remove it using the SWx,,,,!  Command.

5.4 Variable Cycle Special Control

5.4.1 OBJECTIVE

Allows up to three sets of cycle control setpoints based on ranges of make-up conductivity.

Each range of make-up conductivity has a cycles setpoint with a 1% deadband.

Sets the maximum tower conductivity independently of the three make-up ranges.

### 5.4.2 TYPICAL APPLICATION

Sites where the make-up conductivity varies and the limiting hardness or silicon also varies with make-up the conductivity. User sets cooling tower cycles based on tower/make-up conductivity so that as the make-up conductivity varies, the tower/make-up conductivity setpoint changes to prevent scaling.

### 5.4.3 REQUIRED COMPONENTS

Controller software Version 4.0 or later and controller with R2 or RM option.

Controller must be measuring make-up conductivity and controlling the bleed valve on the ratio of Tower-to-Make-up conductivity.

Trackster Version 2.1 or later with Terminal screen option.

As of 05/01 Trackster does not support the ‘VC’ Special Control within View Configuration.

# 5.4.4 INSTALLATION

5.4.4.1 Hardware Installation

Control of cooling tower cycles requires conductivity sensors in both the cooling tower make-up line and the 	cooling tower sump re-circulation line.

5.4.4.2 Software Set-Up –  ‘E’ & ‘F’ Example

The following example assumes that the tower conductivity is connected to input ‘E’, the make-up conductivity connected to input ‘F’ and bleed valve is powered by Relay No.2 which is the typical cycle control set-up for a Flex series controller. The example also assumes that the maximum  tower conductivity should not exceed 3,000uS.

1.Connect to the controller using Trackster at the Configure password level and verify that both the cooling 	tower and make-up conductivities are reading correctly and the Control Equation for the bleed valve is 	set to E/F.

2. Right click on the bleed valve, select Configure Control and key Control-Alt-Shift & you’ll be in the 					Trackster terminal screen

3. Key Enter to get to the command prompt ‘>’

4. Key SW2,,,,VC & Enter

5. Key VC2,300,8.2,700,5.4,1000,4.1,3000 & Enter  & close the  terminal window,

6. Calibrate your tower make-up conductivity across the all three ranges and then above the maximum and 	observe that the control setpoints change with each range.

5.4.5 TECHNICAL – OPERATIONAL NOTES

- A maximum of 4  tower bleed controls with the VC special control are allowed in any one Flex or ‘AS’ series controller. These controls can share the same make-up conductivity sensor.

- Adjust Setpoints: VC dynamically re-writes the controller setpoints as the raw water conductivity changes. Any setpoint changes made in Trackster will be overwritten.	   LCD Adjust Setpoints: This option is blocked. ENTER key provides the same result as PREVious; the current Setpoints are displayed.

- Make-up conductivities must increase from Low Make-up to High Make-up conductivity or an Out-of-Range error occurs and the requested VC command change is rejected.

- A make-up conductivity greater than High Make-up, switches control to the Tower Maximum Conductivity setpoint with a 1% deadband.

- The cycles in each range can be any value. There is no assumption that cycles will decrease as raw water conductivity increases.

- A system alarm ‘Variable Cycles OFF invalid control eqn.’ if the relay control equation does not have two analog sensors separated by either ‘/’, ‘+’ or ‘-‘. This alarm will occur as soon as you change the control equation.

- If you use ‘XCx’ command to remove relay ‘x’ , you will not be able to re-use the VC control on this relay or another relay until you remove it using the SWx,,,,!  Command.

Caution: The bleed control setpoints change as soon as the make-up conductivity moves into the next range. Towers with long holding times may experience scaling conditions as most of the water in the system does not change immediately with a change in make-up conductivity. The HT, Holding Time, special control may be more useful on systems with extended holding times.

5.4.6 COMMAND SYNTAX

The SW command is used to set Variable Cycles special control.

SW[1..8],,,,VC & Enter sets the Special Control on Relay1 to 8 in Flex or 1 to 5 in ‘AS’ series controllers.

Once you have set the special control on the bleed relay you can use the VC command:

VC[1..8],Low Make-up, Low Cycles,Medium Make-up,Medium Cycles,High Make-up,High Cycles, Maximum Tower Conductivity & Enter

Where Low, Medium and High Make-up conductivities set the range for each cycle setpoint

0 – Low         Make-up uS controls at Low Cycles with 1% deadband

Low-Medium  Make-up uS controls at Medium Cycles with 1% deadband

.     Medium-High Make-up uS controls at High Cycles with 1% deadband

Maximum Tower Conductivity controls the bleed, limiting the tower conductivity and providing a default for			 make-up conductivities greater than High Make-up

Typical example:

SW2,E/F,,,VC & Enter

Sets Relay No.2 to cycle control using the ratio of conductivity sensors E & F and sets the Special Control to VC, Variable Cycles. Note that setpoints are not required since they are controlled by the VC defaults until adjusted.

VC2,300,8.2,700,5.4,1000,4.1,3440 & Enter

Sets Relay No,2 to control at 8.2 cycles when the make-up conductivity is less than 300uS, 5.4cycles between 300 & 700 uS and 4.1 cycles between 700 & 1000 uS.

At a tower conductivity greater than 3440uS, the controller will operate the bleed to maintain 3440uS.

5.5 Feed Verification Inventory-ppm Tracking

### 5.5.1 OBJECTIVE

Provides up to two independent feed verification functions per ‘AS’ controller and four per ‘Flex’ controller.

Meters chemical feed in ml, calculates and logs ppm, calculates and logs inventory, displays and logs ml/hour. Supports ml per gallon feed controls and alarms on fail–to-feed.

Alarms locally and pages on low or high, ppm, ml fed and inventory level.

Feed ml and ppm functions are limited to relays controlled by water meters

### 5.5.2 TYPICAL APPLICATIONS

A Feed Verification Meter is installed on the inhibitor chemical feed pump discharge. The Controller is set to feed 10ml every 100 gallons of make-up and display ppm based on the make-up volume and the ratio of the tower to make-up conductivity. The Controller dials out an alarm on low ppm, low tank level and fail to feed inhibitor.

A Feed Verification Meter is installed on the bleach pump discharge at a site where gas blocking of the pump is an operational problem. The Controller is set to feed bleach to maintain an ORP setpoint. The Controller dials out an alarm on low bleach tank level, high feed volume and fail-to-feed bleach.

A DigiPulse  is installed on the LMI biocide pump discharge at a site where regular biocide feed is critical. The Controller is set to feed biocide twice a week. The Controller dials out an alarm on fail-to-feed biocide.

A Bleed water meter is used a Feed Verification signal on a cooling tower bleed. The Controller is set to bleed on conductivity. The Controller dials out an alarm on fail-to-bleed.

### 5.5.3 REQUIRED COMPONENTS

Controller software Version 4.0 or later, controller with R2 or RM option.

Water Meter Based ON/OFF Controls

Controller must be controlling inhibitor feed based on make-up water meter volume and use one of three methods of measuring cycles of concentration:

1. Bleed valve control uses the ratio of tower-to-makeup conductivities

2. Bleed volume is measured by a water meter connected to the controller.

3. Make-up water conductivity is constant allowing a fixed number to be used for cycles of concentration.

Other ON/OFF Controls & Timers

Controller requires a water input configured for use with a Feed Verification Meter, an LMI DigiPulse or in the case of a Fail-to-Bleed application, a Paddle Wheel or Turbine water meter.

Trackster Version 2.1 or later with Terminal screen option.

As of 12/02 Trackster does not support the ‘FV’ special control within View Configuration.

Aquatrac accessory SFX-FV Kit consisting of the Feed Verification Meter, upgrade software chip and controller upgrade code.

# 5.5.4 INSTALLATION

5.5.4.1 Hardware Installation

Refer to Feed Verification Meter, Section 5.6, for meter installation, wiring and verification.

5.5.4.2 Typical Software Set-Up   Q-WaterMeter, I - Inventory & J - ppm Example

The following example assumes:

- That controller inputs Q, I and J are enabled are not being used by the controller for water meters or sensors.

- The Feed Verification Meter is connected to water meter Input ‘Q’.

- Parameter ‘I’ will display the current drum or tank level.

- Parameter ‘J’ will display the current ppm.

- Relay No.1 is being used to feed inhibitor and it’s controlled water make-up meter ‘O’.

- We’re operating the tower at 3.5 cycles

#### Configuration Sequence

- Connect to the controller using Trackster at the Configure password level.

- Right click on the bleed valve, select Configure Control and key Control-Alt-Shift & you’ll be in the			 Trackster terminal screen

- Key Enter to get to the command prompt ‘>’

- Key SW1,,,,FV & Enter

- Key FV1,Q,I,J,C3.5 & Enter  & close the  terminal window,

You have configured the controller to use the Feed Verification Meter connected to input ‘Q’ to monitor the inhibitor feed pump which controlled by water meter ‘O’ and powered by Relay No.1.

As the Feed Verification Meter reads feed volume, it will adjust the Tank Level and display the current level on parameter ‘I’

As watermeter ‘O’ measures tower make-up and the Feed Verification meter ‘Q’ measures chemical feed, ppm will be calculated and displayed and logged in parameter ‘J’

5.5.5 TECHNICAL-OPERATIONAL NOTES

- A maximum of four Feed Verification controls are supported per ‘Flex’  or two per ‘AS’ controller.  Two fully configured FV controls would use two water meter inputs for meters, two water meter inputs for tower make-up volumes and four analog, sensor inputs for Inventory and ppm.

- The DI command displays the Feed Verify option if the option has been installed.

- Feed Verification Meter: Must be connected for FV function and set to Gain =1, Scale=0. The controller applies the controller Gain correction to the Meter counts allowing for fine tuning the 1ml/pulse Meter output and for use of alternative meters or LMI’s DigiPulse.  Alarms can be set on the FV Meter inputs the same way as other water meters.  mL/pulse may be set to 1.15 or 3.26 and the controller software will calculate, volume pumped, ppm & tank levels correctly.

- Feed Verification: Every 10 seconds of chemical pump run time the FV function expects to measure at least 1mL of feed. If 1mL is not measured both the alarm on the FV Meter input and a System Alarm are set.  The user can set an alarm relay an/or dial out response on either alarm.

- Inhibitor ppm: FV requires chemical feed based on a make-up water meter. This meter is used to calculate the volume in ppm calculations. Rate-to-Volume may be used to assign a 4-20mA input to the make-up water meter.

- Inhibitor ppm  - Cycles of Concentration: In addition to make-up volume, FV needs to know the cycles of concentration for ppm calculations. There are three ways set Cycles of Concentration:

  - Fixed: User defines a fixed number of cycles. This works well make-up conductivity constant and a bleed meter or a make-up conductivity do not exist. Zero and negative fixed cycles are rejected & set Cycles = 1.

  - Bleed Volume: Requires a water meter on the tower bleed. Calculates cycles as the ratio of make-up to bleed volumes. Any water meter may be used. There is no software check on the validity of the designated bleed water meter. If you use an incorrect meter, the calculated ppm will understandably incorrect. If the bleed volume is zero, ppm is not calculated. The ppm calculation is updated only when the make-up volume or Feed verification meter updates.

  - Conductivity Cycles: Controllers using the ratio of Tower-to-Makeup conductivity to control the bleed can use the same ratio for cycles. The control equation of a cycles controlled bleed relay is the ratio of conductivities, typically ‘E/F’.  There is no software check of the relay designated for cycles control. You may use any relay with a non-zero control equation.  Every time the Cycles method is changed, ppm is re-calculated from mid-night.

- ppm Calculation & Calibration:

  - ppm calculation starts at midnight based on the water and chemical used that day.

  - The average ppm for each hour is stored in the controller log in the optional parameter, A to N,  used for ppm.

  - ppm is recalculated every 10ml of chemical metered and every 100 Gallons of make-up and whenever the Cycles method is changed.

  - ppm can be calibrated like any other parameter .  Both Offset and Gain can be used to correct for wind losses etc….

  - Setting the ppm parameter in the FV command, sets the parameter compensation to Derived.

- Inventory Calculation:

Inventory is updated every 10ml of chemical metered.

Parameter offset is used to adjust inventory when tanks are re-filled.

Selecting the Calibrate Sensors & Key Current Value? options with the TV remote keypad allows the 			user to enter the current tank level.

This level is decremented by the Feed Verification Meter every 10mL , approximately 0.003 Gallons.

Alarms can be set on inventory level similar to any other parameter.

Setting the Inventory parameter in the FV command, sets the parameter compensation to Inventory.

- Feed ml / gallon:

Inhibitor controls with the FV special control may be set to feed so many mL for every so many Gallons of make-up.

Set the control equation to be O:Q where O = Make-up water meter O to T & Q – FV Meter O to T.  Setpoints may be entered using the TV remote where Volume= Make-up Volume and Time = mL.

Time Owed is now mL and not minutes.

The ‘ST’ Command will correctly display Setpoints in mL and feed owed in mL.

Support for O:P feed mode within Views requires a Trackster update.

- Site Units: Use the ‘SU’ Site Units command to switch from the factory default U.S. Gallons to Metric.  ‘SU’ effects only ppm and inventory calculations. This command is not blocked on controllers without the FV function.

- Activating-Removing FV Special Control; The FV control ppm calculations do not become active until you select a Cycles mode. The FV control may be removed by setting the relay special control to ‘!’ in Terminal mode or None in Trackster.

- Error Trapping:

FV use a lot of controller resources to deliver a range of services. The controller protects users from set-up and re-configuration errors in the following ways:

  - A Parameter used for ppm cannot be assigned to more than one FV control.

  - A Parameter is used for other controls cannot be assigned for Inventory or ppm. Causes ‘Parameter already in use!’ error message.

  - A Parameter used for Inventory, tank level calculations, assigned to more than one FV control to support more than one pump drawing from a common tank.

  - Reconfiguring an inhibitor pump, with FV special control, to non-water meter control, removes the FV special control IF there is analog Parameter set to display ppm.

  - Removing an FV special control, removes Inventory and Derived compensation from the parameters used for Tank Level and ppm logging.

  - Switching the water meter controlling the inhibitor pump, forces ppm recalculation using the new make-up meter volume.

  - Attempting to assign a ppm parameter on relays that are not water meter controlled, causes the ‘ppm requires meter control’ error message.

5.5.6 COMMAND SYNTAX

The SW command is used to set Feed  Verification control.

SW[1..8],,,,FV & Enter sets the Special Control on Relay 1 to 8 in Flex or 1 to 5 in ‘AS’ series controllers.

FV & Enter displays the FV command syntax.

FV[1..8] & Enter displays the current FV configuration. This command is blocked if the FV option is not installed.

DI & Enter displays the installed controller options including the FV option

Once you have set the special control on the inhibitor pump feed relay you use the VC command:

FV[1..8], [Feed Verify Meter O..T],  [Inventory A..N], [ppm A..N],

C[Fixed # of Cycles] or  [Bleed Meter O..T ] or  [Bleed Control Relay 1..8] & Enter

Where

[Feed Verify Meter O..T] 		Water meter input where Feed Verification Meter connects.

[Inventory A..N]					OPTIONAL: Parameter which logs & displays tank level

[ppm A..N]							OPTIONAL: Parameter which logs & displays ppm

Select one of:

C[Fixed # of Cycles] 			Fixed number of cycles, displayed to 2 decimals

[Bleed Meter O..T ] 			Tower or process bleed meter

[Bleed Control Relay 1..8]   Bleed solenoid relay controlled on the ratio of tower to make-up											 conductivity.

5.5.7 HYPERTERMINAL SCREEN DISPLAY

| HyperTerminal Display support on ml Feed in bold Command: ST1,2,Q,J & Enter | Notes |
| --- | --- |
| STATUS Aquatrac Instruments Date: 1/3/80 SMARTFlex Controller Time: 4:13:44 Inhibitor Pump 1 Pump Volume@100 Interlock Status #1State ON Pump mL @10 Operating Time This Actuation Control Equation: O:Q = 1900 0.2 Minutes Switch Interlock Operating Time Today 2U 3.9 Minutes Special Control Feed Volume Owed Feed Verify on Q 44.0 mL Bleed Valve 1 Turn ON @2000.00 Interlock Status #2State OFF Turn OFF@1975.00 Operating Time This Actuation Control Equation: I = 99.962 0.0 Minutes Switch Interlock Operating Time Today U 0.0 Minutes Special Control Operating Time Owed 0.0 Minutes FV Meter 124 PPM Calc 169.644 | Feed in mL New ‘:’ control equation New control Owed mL. No change In other relays or controls FV Meter on ‘Q’ In mL & ppm on ‘J’ |

5.6 Feed Verification Meter Installation

### 5.6.1 OBJECTIVE

Details installation of the Feed Verification Meter required for inhibitor feed verification function.

Part#’s SFX-FV, SFX-FV2 & SFX-FL

### 5.6.2 REQUIRED COMPONENTS

- Feed Verification accessory kit consisting of the Feed Verification Meter, upgrade software chip and controller upgrade code.

- Controllers shipped with the SFX-FV, SFX-FV2 & SFX-FL options should skip Step 3.2 which upgrades controller software.

- A solenoid type chemical feed pump: LMI or PulsaFeeder type rated 8-24GPD

- If the pumps are not beside the controller, you may have to extend the Feed Verification Meter cabling using 3 conductor or 2 pair, AWG 22 cable.

# 5.6.3 INSTALLATION

5.6.3.1 Hardware Installation

Install the Feed Verification Meter on the discharge side of the inhibitor pump between the pump and injector and tighten the tubing 3/8” fittings.

Plug the inhibitor pump into a hot plug and verify that the tubing connection to the Feed Verification Meter seal.

The Feed Verification Meter can be oriented with horizontally or vertically. Locate the Meter so that the Red & Green LEDs are visible.

SFX-FL Kits

‘DigiPulse’ use is limited to installation on the output of LMI pumps. Follow the instructions

included with the ‘DigiPulse’

5.6.4 SOFTWARE UPGRADE / Skip this step if new Controller

- If you are running Trackster and the controller is running & has either the serial port or modem 	options, connect to the controller and use the Save option under the Controller menu option to save the current controller configuration to your PC.

- Unplug the Flex or AS controller power cord.

- Open the enclosure door and turn OFF the power switch on the right, bottom of the circuit board installed in the enclosure door.

- STATIC DAMAGE: Touch the grounded aluminum controller backplate to discharge static before touching controller electronics. WARNING: Static electricity can fail a controller. This fault is preventable and is therefore not covered by the manufacturer’s warranty.

- Using a small screwdriver, remove the existing software chip installed in a socket on the

sub-board located in the top, center of the controller. Be careful that you are removing the chip and not the chip socket. This chip will be labeled either Smart ‘AS’ OR Smart ‘Flex’ with the Version#

6. Install the upgrade chip, ensuring that the label is oriented the same way as the chip you removed.   The chip label text should be oriented the same way as the controller serial 	number chip to the left of the upgrade chip.

CAUTION:  Ensure you fully insert the upgrade chip without bending any of the pins.

Ensure that the chip is correctly oriented and that all 32 pins are inserted.

7. Turn on the controller power switch at the bottom, right of the controller board and plug in the controller power cord.

8. The LCD display should display the POWER UP message for several seconds and then start to 	scroll through all of the operating parameters.

WARNING: If you do not see the POWER UP message on power ON. Turn OFF the controller and review the upgrade instructions.  It’s likely that the upgrade chip is incorrectly installed or an ‘AS’ chip has been installed in a ‘Flex’.

A chip installed upside down will be destroyed and cannot be re-installed.

The controller will reset itself to its default state when it detects upgraded software.

After a software upgrade, you’ll have to re-enter setpoints, calibration, water meter gallons/contact, biocide timing and reset the time and date...

Use Trackster’s Restore feature to re-load the controller configuration, if you were previously able to save the configuration.

5.6.5 CABLING & CONTROLLER CONNECTION

Turn OFF the controller.

SFX-FV Kit

Cable the three conductor feed verification meter cable to the controller and an unused water meter input, typically ‘Q’

Connect RED to QP, WHITE to Q+ & BLACK to Q-.

SFX-FV2 Kit

Cable the three conductor feed verification meter cables to the controller and to unused water meter inputs, typically ‘Q’ for Inhibitor No.1 and ‘T’ for Inhibitor No.2

Inhibitor No.1 meter: Connect RED to QP, WHITE to Q+ & BLACK to Q-

Inhibitor No.2 meter: Connect RED to TP, WHITE to T+ & BLACK to T-

SFX-FL Kit

Cable the two conductor DigiPulse cables to the controller and to unused water meter inputs, typically ‘Q’ for Inhibitor No.1 and ‘T’ for Inhibitor No.2

Inhibitor No.1 meter: Connect WHITE to Q+ & BLACK to Q-

Inhibitor No.2 meter: Connect  WHITE to T+ & BLACK to T-

Turn ON the controller & verify that the RED POWER LED turns ON on each Feed Verification Meter.

5.6.6 PUMP SET-UP & VERIFY METER CONNECTION

Set the inhibitor pump(s) to 100% stroke & 100% frequency.

Plug the feed verified pump into a hot outlet.

Each time a mL is pumped, the GREEN SIGNAL LED will flash. Reduce the pump frequency and note that several strokes may be required per mL fed.

SFX-FL Kit

Verifying DigiPulses requires serial or modem connection to the controller with Trackster

5.7 Time Modulation Control

### 5.7.1 OBJECTIVE

Details the operation of the ‘TM’, Time Modulation, chemical feed pump duty cycle special control

The ‘TM’ command targets plating and metal finishing applications where a pump or solenoid ON time is 	controlled or ‘modulated’ by the value of the controlling sensor with respect to the Turn ON & OFF Setpoints.

### 5.7.2 FUNCTION

Switches pump power ON/OFF from 0% ON time to 100% ON time between the control setpoints.

Allows REVERSE control to be set which inverts the 0% and 100% setpoints.

User can set the 0-100% PERIOD which defaults to 60 seconds.

Feed Modulation:

Controller set to turn ON at 2000uS and OFF at 2500uS. Reverse control selected.

Modulation period = 60 seconds.

At 2000uS and less, bleed is ON for 60 seconds in every 60 seconds.

At 2500uS bleed is ON for 1 second in every 60 seconds.

At 2501uS bleed is OFF.

Bleed Modulation:

Controller set to turn ON at 2500uS and OFF at 2000uS,.

Modulation period = 60 seconds.

At 2500uS and greater, bleed is ON for 60 seconds in every 60 seconds.

At 2000uS bleed is ON for 1 second or less in every 60 seconds.

At 1999uS bleed is OFF.

Caustic Feed Modulation:

Controller set to turn ON at  8.5pH and OFF at 8.0pH,.

Modulation period = 120 seconds.

At pH 8.5 and above the caustic pump is ON for 120 seconds in every 120 seconds.

At pH 8.0 the caustic pump is ON for 1 second or less in every 120 seconds.

At pH 7.99 the caustic pump is OFF.

Acid Feed Modulation:

Controller set to turn ON at  8.0 pH and OFF at 9.0pH,. Reverse control selected.

Modulation period = 100 seconds.

At pH 8.0 and below, the acid pump is ON for 100 seconds in every 100 seconds.

At pH 9.0 the acid pump is ON for 1 second or less in every 100 seconds.

### At pH 9.01 the acid pump is OFF.

5.7.3 COMMAND SYNTAX

The Time Modulation, ‘TM’ option is entered in the special control field of the ‘SW’ switch command using the 	syntax:

###### SWx,,,,TMy where x = Relay#1..8 and y= Period time in seconds, default=60 sec.

Example:  SW1,,,,TM & Enter  sets the 0-100% period to the 60 second default.

Example SW1,,,TM100 & Enter   sets the 0-100% modulation period to 100 seconds.

Notes:

- Setting the control equation to any water meter, removes Time Modulation

- Attempting to set the Time Modulation special control on a switch controlled by a water meter displays ‘meter illegal with special control’

- Removing the control equation on a switch with Time Modulation, removes the Time Modulation special control.

5.7.4 ‘ON’ TIME RESOLUTION & RECALCULATION

- The controller calculates ON time in seconds, as an integer. The change in sensor value required to increase the ON time by one second is a function of both the ON-OFF difference and the PERIOD.

- EXAMPLE: Turn  ON = 2000uS, 	Turn OFF= 1000uS,  PERIOD = 60 seconds

| Conductivity | ON Time (secs) | Floating Point Calculation converted integer |
| --- | --- | --- |
| 1000 | 0 | 60 x (1000 – 1000) / (2000–1000) = 0 |
| 1016 | 0 | 60 x (1016 – 1000) / (2000–1000) = 0.96 |
| 1018 | 1 | 60 x (1018 – 1000) / (2000–1000) = 1.08 |
| 1036 | 2 | 60 x (1036 – 1000) / (2000–1000) = 2.16 |
| 1508 | 30 | 60 x (1508 – 1000) / (2000–1000) = 30.48 |
| 1984 | 59 | 60 x (1984 – 1000) / (2000–1000) = 59.04 |

- The ON time is recalculated at the end of every OFF time.

CAUTION: Do not use the TM special control for control of processes where the sensor traverses between setpoints in less than 5-10 PERIODS; poor control will result.

5.7.5 DIAGNOSTIC – ‘ST’ COMMAND

- The ‘ST’ command will count down both ON and OFF times in seconds in the Special Control field.

- Modulated 25  will be displayed if the ‘TM’ special control is set and you have either 25 seconds of ON or OFF time remaining. The relay state will change when the time count down time zeroes.

- Clear Alarms starts a new OFF time.

5.7.6 LIMITS & OUT-OF-LIMITS RESPONSE

- Minimum 0-100% period is 60 seconds. Attempting to set the period to less than 60 seconds, sets the period to 60 seconds.

- Maximum period is 3600 seconds. Attempting to set the period to more than 3600 seconds, sets the period to 3600 seconds.

- Setting the control equation to a water meter disables the control. Attempting to set the control on a relay with a water meter control, causes an error message.

- Clearing alarms resets the current cycle and starts another ON time. Owed time is zeroed.

- Priming adds time owed to the ON calculated by the TM special control.

5.7.7 ALARMS & DATA LOGGING

- There is no change in feed limit timer or data logging. The controller logs the pump ON time and times out on minutes per actuation exceeded and minutes per day exceeded.

- The controller will log the actual pump run time and will display relay ON & OFF state correctly while modulating the pump or solenoid between setpoints.

5.8 Timed Cycling Control

### 5.8.1 OBJECTIVE

Details the operation of the ‘TC’, Timed Cycling, chemical feed pump intermittent feed, special control.

The ‘TC’ command targets swimming pool control where there is a long time delay between feed and detection 	of the feed at the controlling sensor.

The ‘TC’ command may also be used to base feed a chemical by setting a pump ON time and a PERIOD in 	minutes.

### 5.8.2 FUNCTION

Switches pump power ON for a user defined time in every user defined PERIOD.

Whenever the control sensor is between Setpoints, pumps and valves controlled by a sensor, will Time Cycle.

User sets the ON & PERIOD time in minutes to reflect each sites’ pump size and time delay.

Oxidant Feed Cycling:

Oxidant control set to turn ON at 300mV and OFF at 500mV.

Period = 30 minutes, ON time = 5 minutes

When the ORP is between 300mV and 500mV the oxidant pump or solenoid is ON for 5 minutes

in every 30 minute period.

###### Base Feeding:

A biocide is fed for 2 minutes every 60 minutes.

A sensor and setpoints are required for Timed Cycling. Typically the system flowswitch input U…Z, is used 	as the control equation with the setpoints in ON time in seconds @ ON=100000 & OFF=0

When base feeding, the sensor is selected and setpoints set so the sensor is always between the Turn On & Turn OFF setpoints.

Priming and Biocide feed timing may still be used to slug feed.

User set biocide timing will be added to Timed Cycling ON times.

Notes:

- Outside of the TURN ON – TURN OFF window, the pump is always OFF.

- Setting ‘REVERSE’ control disables Timed Cycling.

- Setting the control equation to any water meter, removes Timed Cycling

- Attempting to set the Timed Cycling special control on a switch controlled by a water meter displays ‘meter illegal with special control’

- Removing the control equation on a switch with Timed Cycling, removes the Timed Cycling special control.

5.8.3 COMMAND SYNTAX

The ‘TC’ option is entered in the special control field of the ‘SW’ switch command using the syntax:

###### SWx,,,,TCy/z where x = Relay#1..8, y= PERIOD time in minutes & z= ON time in minutes.

Example: SW1,,,TC20/4 & Enter

Every 20 minutes, the pump controlled by Relay No.1 will be ON for 4 minutes.

The controller will respond with the ON time and the PERIOD time.

Keying SW1 & Enter will display current settings for ON time & PERIOD

5.8.4 CURRENT STATE MONITORING

The ST command will count down the current ON or OFF time in fractional minutes in the Special Control 	section of the ST response screen.

Example: ST1,6 & Enter will display the current state of relays No.1 & No.6.

5.8.5 LIMITS & OUT-OF-LIMITS RESPONSE

- Timing is reset at midnight. A new PERIOD starts at midnight.

- Maximum PERIOD in TC mode is 360 minutes. Attempting to set the PERIOD to more than 360 minutes, sets the PERIOD to 360 minutes.

- Periods greater than 6 hours can be set using the existing biocide timing.

- Setting the ON time to greater than the PERIOD, sets the ON time equal to the PERIOD time.

- Setting the ON or PERIOD to time less than 1 minute, sets the PERIOD to 1 minute

- Clearing alarms restarts the PERIOD and starts another OFF time. Owed time is zeroed.

5.8.6 ALARMS & DATA LOGGING

- There is no change in feed limit timer or data logging when the ‘TC’ special command is used.  The controller logs the pump ON time and times out on minutes per actuation exceeded and minutes per day exceeded.

- The controller will log the actual pump run time and will display relay ON & OFF state correctly while time cycling the pump or solenoid between setpoints.

5.9 Version 4 ‘AS’ & Flex Controller Software

### 5.9.1 OBJECTIVE

Details the added functions and changes in existing function operation available in Flex & ‘AS’ controller operating software, Version 4.

### 5.9.2 NEW COMMAND SUMMARY

Rate-to-Volume:  Converts a 4-20mA input on both GPM & LBH to Gallons & Pounds of Steam. assigns the converted value to a water meter input and executes ON/OFF pump control. Adds the ‘R’ analog input compensation. Typical applications & details in AN010-05.

Variable Cycles: Supports cycle control with up to three ranges of make-up conductivity and a maximum tower conductivity override. Adds VC command & VC Special Control - Typical applications & details in AN010-06

Feed Verification: Calculates ppm, Drum level, alarms on fail-to-feed. Support for 1ml/pulse chemical feed metering. Adds FV command & FV Special Control. Requires FV option ON in controller options. Typical applications & details in AN010-07 & hardware installation in AN010-08.

### 5.9.3 TRACKSTER SUPPORT

Most of the upgraded and new features in Version 4 controller software will display correctly on the current Version of Trackster.

Feature set-up and VC setpoint adjustment will require an updated version of Trackster.

Until the Trackster upgrade is issued, use Trackster Terminal.

Access Trackster Terminal by connecting at the ‘configure’ level password, right click on any pump or valve & select Configure Control. Key Control-Alt-Shift and Trackster Terminal will pop up.  Key Enter to get a command prompt, ‘>’ and key the terminal commands detailed in each of the new function’s application notes.

### 5.9.4 CONTROLLER FUNCTION CHANGES

Alarm on No Flow:

Use the PA command to alarm on no-flow. Setting an alarm on no-flow does not affect any other status switch functions; interlocking function and minutes ON data is unchanged.

Factory Default: All ‘cooling tower’ flowswitches set to alarm after 5 minutes of no flow.

Interlock on boilers and other dry contact defaults are unchanged.

Adjust alarms on flowswitches to set trip time >1440 to bypass Alarm on No Flow

LCD & Trackster Display: If Alarm on No Flow is set, both Time ON & Time OFF count up 	on both LCD & Trackster display with ON & OFF displaying current state.

Use the PA command to set the Alarm on No Flow & to view current state of Flow/No Flow

Example PAU,,1 & Enter sets flowswitch U to alarm on no-flow. Alarm on no flow cannot be selected using the TV Remote Keypad.

Trackster & the AL command may be used to set the delay between loss of flow and dial out or alarm relay trip.  If you do not set Alarm on No Flow, then the alarm will trip after the status contacts have been closed for more than the alarm time setting.

Boiler Conductivity Calibration: Remote Keypad single point calibration of boiler conductivity updates the LCD immediately instead of waiting for the next timed sample.

If the calibrated conductivity is above blowdown setpoint, a new sample occurs as soon as the calibration is accepted by keying Enter.

This change was made to remove the perception that users needed to calibrate boiler conductivities twice to have the calibration take effect.

Control on Dry Contact Sets: It’s always been possible to control on Status inputs U to Z using the contact ON time in seconds as a Setpoint. Version 4  blocks the use of Relay numbers in the control equation while allowing control by flowswitches and other dry contact sets.  The controller displays time in Minutes not seconds. If you wish a relay to turn ON 5 minutes after a status switch contact set closes, the Setpoint would be 300 seconds.

Delay on Alarm = 5 minutes: The default factory delay on alarm for all analog parameters has been set to 5 minutes. Delay on alarm cannot be adjusted using the TV Remote keypad and the previous long delays on alarm were unacceptable for some users. Alarms on analog parameters do not prevent pumps and valves from operating.

Dual Tower Controller Inhibitor Feed: TV Remote keypad INHIBITOR CONTROL Option now switches from water meter to bleed based feed options. For example, Tower2 Inhibitor on Relay #5 may be switched to Bleed then Feed using the Tower2 Bleed on Relay#6. Biocide Lockout for tower No.2, locks out Relay#6 Bleed. PREVious key shows the correct bleed solenoid for each tower.

Enabling Analog Inputs: Enabling any analog inputs A to N in Trackster or Hyperterminal will set the Gain = 1 & Offset=0 only if the previous Gain is zero. Allows  the user to turn ON unused analog inputs and to calibrate without leaving Trackster.  Previously configured inputs that have been temporarily disabled would  be unchanged since they would have non-zero Gains.  This change does not affect any other input parameter other than Gain; description, units, alarms are unchanged.

Feed on Water Meter Setpoints: The TV Remote keypad ADJUST SETPOINTS now allows you to set water meter GAL up to 9,999 Gallons. Previously you were limited to 999 Gallons. This change will help sites that are feeding on Steam Volume and using Rate-to-Volume on Steam Demand where numbers greater than 999 are common.

Feed Verification & Inhibitor Control: The TV Remote keypad INHIBITOR CONTROL? Option is disabled when the FV special control is active to prevent users from switching to Bleed & Feed, Bleed then Feed or Percentage Time. If you key ENTER on the FV Inhibitor Pump, you’ll get the ‘Feed Verification ON meter only control’ LCD message. Removing FV special control allows all four feed modes.

The controller automatically removes the FV control if you switch inhibitor feed from water meter control using Trackster.

Filling Chemical Tanks: Any sensor with INVENTORY compensation set using the FV command will allow single point entry of tank level using the TV Remote keypad CALIBRATE SENSORS? Option and selecting Key Current Value?. The Feed Verification Meter will reduce tank level as it meters feed volume.

The Tank filling function is not currently supported in Trackster.

Inhibitor Minutes ON Feed Limit Timer: When an inhibitor feed exceeded it’s ON timer, it reset and set an alarm on the controlling water meter. This was confusing and has therefore been removed and replaced with System Alarm #3  “Feed Pump time limit exceeded”.

This alarm will not report with the correct descriptive text until Trackster is updated to accommodate the revised system alarms.

ORP Calibration: TV Remote keypad CALIBRATE SENSORS Option now allows single point on ORP by adjusting offset. Gain is fixed at –1. assumes any sensor with units = mV is an ORP sensor & offers the KEY CURRENT VALUE option on calibration.

Percentage Time: Time owed does not increase if the flowswitch interlocking the relay is OFF. Base feed, percentage time controls, prior to Version 4, added time owed to the relay when the interlocking flowswitch was OFF.

Set Units: The SU command is used only with the FV option to calculate ppm and drum levels. Factory default is U.S. units, which assumes that the make-up meter & chemical inventory measures in Gallons. Setting SU to metric, assumes the make-up meter & chemical inventory measures in Liters. The SU command ignores the user set units on the make-up meter only for the purposes of ppm  & chemical inventory calculations. Use of an SU, generic units command permits users to set units as they wish without corrupting ppm & tank level calculations.

The SU command is not currently supported in the current version of Trackster.

Variable Cycles: Disables LCD setpoints while allowing the user to view the current setpoints, which are changed by the controller as the make-up conductivity varies. VC is only useable in controllers with the R2 & RM options since Trackster is required for setpoint in each make-up conductivity range. System Alarm No.4 is set whenever the user switches a relay operating a VC special control from the ratio or conductivities.  The VC control uses the second conductivity in a typical ‘E/F’ control equation as the make-up conductivity for ranging purposes.

The VC special control setpoints are not viewable or adjustable from within the current version of Trackster.

XC Configurations: XC[A..J]24 may be used to set a  Rate-to-Volume input on an ‘AS’ with XC[A..N]23 or XC[A..N]24 used on a Flex.   Warning: Since control resources are assigned whenever the FV special control is selected, it is not possible to use the XC command to factory set an FV special control. A controller that has a checksum fault OR a factory reset, will lose all FV controls. While this fault is rare, FV controls users should use Trackster’s SAVE-RESTORE option to save a copy of the current controller configuration.

5.9.5 NEW in Version 4.3

Version 4.3 of the controller operating software includes a number of new controls and enhancements to existing controls. Section 5.9.5 summarizes the changes detailed in each the preceding sections of this manual

Feed Verification: FV – Reference 5.6

The number of Feed Verifies per Flex series controller has been increased from 2 to 4.

‘AS’ series controllers remain limited to 2 Feed Verifies reflecting the lesser number of water meter and 4-20mA inputs available for use with Feed Verification.

Feed Verification can now be used with any ON/OFF control: oxidants, acid feeds, biocides, bleeds…  To provide fail to feed alarms and inventory calculations.

Ppm calculations and ‘mL’ per volume feed’ controls remain limited to those relays controlled by water meters.

Note: FV is a ‘Special Control’. One Special Control can be set on each controller relay. If you are using the FV, Special Control for an Oxidant, the Timed Event Special Control is not available. Similarly, the Lockout & Prebleed Special Controls cannot be used on Biocides with an FV Special Control.

Timed Modulation: TM – Reference 5.7

The ‘TM’ command targets plating and metal finishing applications where a pump or solenoid ON time is controlled or ‘modulated’ by the value of the controlling sensor with respect to the Turn ON & OFF Setpoints.

The controller switches pump power ON/OFF from 0% ON time to 100% ON time between the control setpoints.

REVERSE control can be set which inverting the 0% and 100% setpoints.

# Timed Cycles: TC – Reference 5.8

The ‘TC’ command targets swimming pool control and sites where there is a long time delay between feed and detection of the feed at the controlling sensor. It also be used to base feed a chemical by setting a pump ON time and a PERIOD in minutes.

6. Sensor Specifications & Cabling			See Notes for cabling & installation guidelines

| Measures | Aquatrac Part No. | Mechanical Specification | Electrical Specification | Notes |
| --- | --- | --- | --- | --- |
| Conductivity Ambient | A261200 | 5/8” Diameter sensor x 4.1” long. Black Epoxy body, 0-125F Requires ¾” NPT polyethylene entry fitting – Part# A261201. Rated 100psi. @ 125F Installed in ¾” PVC SCH80 threaded ‘T’ or immersed | Contact type, graphite electrodes. Sensor Drive 50-200mV AC. Thermal Drive 0.5mA @ 12VDC. 10mV/K electronic thermal compensation. 10ft of AWG22, Black, Red, Green, White silver jacketed cable. Un-terminated, tinned ends. Identified by blue sleeve on cable at sensor body. | 1 |
| Conductivity Ambient | A261003 | 5/8” Diameter sensor x 4.1” long. Black Epoxy body, 0-125F Requires ¾” NPT polyethylene entry fitting – Part# A261201. Rated 100psi. @ 125F Installed in ¾” PVC SCH80 threaded ‘T’ or immersed | Contact type, graphite electrodes. Sensor Drive 50-200mV AC. Thermal Drive 0-12 VDC. 500 ohm, NTC thermistor thermal compensation. 10ft of AWG22, Black, Red, Green, White silver jacketed cable. Un-terminated, tinned ends. | 2 |
| Conductivity Boiler & Condensate 250 psi MAX | A261000 A261000-CS | 3/4” NPT sensor x 2.8” long. Glass filled Teflon, carbon steel construction , 250psi steam. Requires ¾” NPT steel SCH80 ‘T’ entry fitting. Sensor installed flush with entry ‘T’ sidewall. A26100-CS includes ¾” conduit fitting on end of sensor. | Contact type, steel electrodes. Sensor Drive 50-200mV AC. Thermal compensation via sampling control. 10ft of AWG22, Black, White, Teflon & Teflon jacketed cable. Un-terminated, tinned ends. | 3 |
| Conductivity Boiler 350 psi MAX | A261CHP | 3/4” NPT sensor x 2.8” long. Glass filled Teflon, carbon steel construction , 350psi steam. Requires ¾” NPT steel SCH80 ‘T’ entry fitting. Sensor installed flush with entry ‘T’ sidewall. | Contact type, steel electrodes. Sensor Drive 50-200mV AC. Thermal compensation via sampling control. 10ft of AWG22, Black, White, Teflon & Teflon jacketed cable. Un-terminated, tinned ends. | 3 |
| Conductivity Hot water OR High Pressure | A261016 A261017 | 3/4” NPT sensor x 2.8” long. Glass filled Teflon, carbon steel construction , 250psi 300F. Requires ¾” NPT steel SCH80 ‘T’ entry fitting. Sensor installed flush with entry ‘T’ sidewall. | Contact type, steel electrodes. Sensor Drive 50-200mV AC. 10ft of AWG22, Black, Red, Green, White silver jacketed cable. Un-terminated, tinned ends. A261016 Identified by blue sleeve on cable at sensor body. Thermal Drive 0.5mA @ 12VDC. 10mV/K electronic thermal compensation. Electrically equivalent to A261200 A261017 Identified by black sleeve on cable at sensor body. 500 ohm, NTC thermistor thermal compensation. Electrically equivalent to A261003 | 1 |

See Notes for cabling & installation guidelines

| Measures | Aquatrac Part No. | Mechanical Specification | Electrical Specification | Notes |
| --- | --- | --- | --- | --- |
| Conductivity & Flowswitch | S2-SCF | Sensor & flowswitch integrated with full union entry 3 ½” Wide at ‘T’ x 6” High at cable entry. Rated 125psi. @ 125F Includes PVC-epoxy sensor, ¾” SCH 80, PVC slip ‘T’ & SCH80 union. | Contact type, graphite electrodes. Sensor Drive 200mV AC. Thermal Drive 30mA @ 12VDC. 100ohm thermistor thermal compensation. 10ft of AWG22, Black, Red, Green, White: silver jacketed cable. Un-terminated, tinned ends. | 4 |
| Corrosion Rate | SFT-CR SAT-CR | 5/8” Diameter sensor x 5.3” long with coupons installed. 2 x #4-40 brass coupon mounts. Black Epoxy body, 0-125F Requires ¾” NPT polyethylene entry fitting – Part# A261201. Rated 100psi @ 125F Installed in ¾” PVC SCH80 threaded ‘T’ | Linear Polarization Type Sensor Drive 0-10mV DC. 10ft of AWG22, Black, Red silver jacketed cable. Un-terminated, tinned ends. Software selected conductivity and alloy compensation. | 5 |
| Flowswitch | A261403 | ½ GPM trip, +/-20% ¾” NPT, glass reinforced polypropylene. 100psig @ 70F & 50psig @ 180F Orient vertical, inlet down. | SPST, N.O. contacts limited to 5mA @ 5VDC by controller. With 10ft. of two conductor AWG22 cable, un-terminated, tinned ends. | 6 |
| ORP Commercial | A261105 | 12mm Diameter (1/2”) sensor. Red Epoxy body, 0-80C Requires ¾” NPT polyethylene entry fitting– Part# A261101. Rated 100psi. Installed in ¾” PVC SCH80 threaded ‘T’ | Single junction, sealed. Un-amplified, 1mV/mV With 20ft. of RG174LN coaxial cable, un-terminated, tinned ends. Cable tagged red | 7 |
| ORP Industrial | ORP—FF | ¾” NPT each end, 6.3” Long CPVC, 0-80C, 100psi, Probe insertion 2” from threaded end. | Double junction, flat faced, sealed. Un-amplified, 1mV/mV With 20ft. of RG174LN coaxial cable, un-terminated, tinned ends. Cable tagged red | 8 |
| pH Integral Amplifier Low Temperature | SXT-GXP | 12mm Diameter (1/2”) sensor. Blue Epoxy body, 0-80C Requires ¾” NPT polyethylene entry fitting Part# A261101. Rated 100psi. Installed in ¾” PVC SCH80 threaded ‘T’ supplied with solution ground. 1 Year battery life | Single junction, sealed. 58mV/pH, rated 0-13pH. With 20ft. of RG174LN coaxial cable, un-terminated, tinned ends. Cable tagged yellow Sleeve @ sensor 5733526PB Use in place of MEXTPH amplifier | 9 |
| pH Commercial | A261100 | 12mm Diameter (1/2”) sensor. Blue Epoxy body, 0-80C Requires ¾” NPT polyethylene entry fitting Part# A261101. Rated 100psi. Installed in ¾” PVC SCH80 threaded ‘T’ supplied with solution ground. | Single junction, sealed. Un-amplified, nominally 58mV/pH rated 0-13pH. With 20ft. of RG174LN coaxial cable, un-terminated, tinned ends. Cable tagged blue | 9 |

| Measures | Aquatrac Part No. | Mechanical Specification | Electrical Specification | Notes |
| --- | --- | --- | --- | --- |
| pH High Temperature | A261103 | ½” NPT each end, 6.5” nominal length. Stainless Steel, 0-105C, 32-220F Probe insertion 2” from threaded end. | Double junction, flat faced, sealed. Un-amplified, nominally 58mV/pH rated 0-12pH. With 20ft. of RG174LN coaxial cable, un-terminated, tinned ends. | 10 |
| pH Industrial | A261102 | ¾” NPT each end, 6.3” Long CPVC, 0-80C, 100psi, Probe insertion 2” from threaded end. | Double junction, flat faced. Un-amplified, nominally 58mV/pH rated 0-12pH. With 10ft. of RG174LN coaxial cable, un-terminated, tinned ends. Cable tagged blue | 11 |
| Water Meter Contact Head | WM.75 to WM2 | In-line water meters from ¾” to 2” FPT fittings. Brass. | SPST, N.O. contacts limited to 5mA @ 5VDC by controller. Requires installer supplied two conductor AWG22, shielded cable. Gallons/contact varies with meter size. | 12 |
| Water Meter Paddlewheel | WMP.75 to WMP4 | Insertion Paddlewheels from ¾” to 4”. Larger sizes available. ¾” to 2” supplied with installation section of PVC pipe. 3” & 4” supplied with pipe clamp for PVC or Steel. | Open drain limited to 5mA @ 5VDC by controller. 12VDC power supplied by controller. Requires installer supplied three conductor AWG22, shielded cable. WARNING Do not reverse RED & WHITE wires, non-warranty sensor failure occurs | 13 |

| # | Notes |
| --- | --- |
|  | Cabling Guidelines. Multiple sensors and sensor types may be mixed in any one conduit. Do not mix sensor cables and 120VAC or 24VAC power in a single conduit. Connect sensor cable shields to the controller electrical ground available at the bottom, left of the enclosure aluminum backplate. The coaxial outer conductors of pH & ORP sensors carry signal and are not shields. PVC conduit does not provide electro-magnetic shielding. |
| 1 | Cooling tower conductivity sensor with displayed temperature. Resolution varies with application, typically 1uS. May be extended to 350ft from controller, 4 x AWG22 cable. |
| 2 | Cooling tower conductivity sensor without displayed temperature. Resolution varies with application, typically 1uS. May be extended to 350ft from controller, 4 x AWG22 cable. |
| 3 | Boiler conductivity sensor Resolution varies with application & thermal compensation technique, typically 1uS May be extended to 250ft from controller, 2 x AWG22 cable. |
| 4 | Conductivity-Flow Sensor Resolution varies with application & thermal compensation technique, typically 1uS May be extended to 50ft from controller, 4 x AWG22 cable. |

| # | Notes |
| --- | --- |
| 5 | Corrosion Rate Sensor May be extended to 200ft from controller, 2 x AWG22, shielded cable. |
| 6 | Flow Sensor Usually installed at the controller for maintenance, test & inspection. May be extended to 200ft from controller, 2 x AWG22, shielded cable. |
| 7 | ORP: Commercial & Light Industrial Cooling Towers May be extended to 50ft. from the controller without a buffer amplifier using 2 x AWG22, shielded cable. Buffer amplifier Part# MEXTPH powered by controller 12VDC & cabled 3 x AWG22, shielded. |
| 8 | ORP: Industrial Cooling Towers & Waste Water May be extended to 50ft. from the controller without a buffer amplifier using 2 x AWG22, shielded cable. Buffer amplifier Part# MEXTPH powered by controller 12VDC & cabled 3 x AWG22, shielded. |
| 9 | pH: Commercial & Light Industrial Cooling Towers May be extended to 25ft. from the controller without a buffer amplifier using 2 x AWG22, shielded cable. Buffer amplifier Part# MEXTPH powered by controller 12VDC & cabled 3 x AWG22, shielded. Requires solution ground, AWG18 green x 10ft. supplied with entry fitting and terminated to controller AC power ground. Part SXT-GVP may be used in place of MEXTPH. Extend buffered sensor in 2 x AWG22 shielded And schedule to replace annually |
| 10 | pH: Condensate May be extended to 25ft. from the controller without a buffer amplifier using 2 x AWG22, shielded cable. Buffer amplifier Part# MEXTPH powered by controller 12VDC & cabled 3 x AWG22, shielded. Ensure controller grounded for sensor solution ground. |
| 11 | pH: Industrial Cooling Towers & Waste Water May be extended to 25ft. from the controller without a buffer amplifier using 2 x AWG22, shielded cable. Buffer amplifier Part# MEXTPH powered by controller 12VDC & cabled 3 x AWG22, shielded. Requires solution ground, AWG18 green x 10ft. supplied with entry fitting and terminated to controller AC power ground. |
| 12 | Contact Head Water Meters Make-up, bleed and closed loop water meters may be remote from controllers. Ensure that meter cabling is two conductor shielded and that the shields are connected to the controller AC ground. Long, unshielded cables to NO contact sets routed in non-metallic conduit are antennas and are very noise sensitive. Contact head meters are usually not used in lines over 1”. Insertion paddlewheels are lower cost. |
| 13 | Paddlewheel Water Meters Make-up, bleed and closed loop water meters may be remote from controllers. Paddlewheel meter cabling may be extended to a minimum of 1,000ft. cabled 3 x AWG22, shielded. Aquatrac controllers connect directly to Seametrics and other open drain & open collector meters. WARNING: Do not reverse RED & WHITE meter wires. Non-warranty meter sensor failure will occur. |