Safety:

Unplug the controller before opening the controller enclosure.

A 120VAC Electrical shock hazard exists on the lower controller circuit board when the controller is plugged in and the enclosure door is open.

This Controller:

Powers and controls chemical feed pumps for inhibitor, oxidant and sulfuric acid.

Powers and controls the cooling tower bleed solenoid.

Measures tower conductivity, temperature, ORP and pH using sensors supplied with the controller.

Measures make-up and bleed water meters.

Uses a flowswitch or jumper to stop bleed and chemical feed when tower flow stops.

Power and control for four biocide pumps.

Measures dual boiler conductivity with sensors supplied with the controller.

Power and control for two boiler blowdown valves.

Two 4-20mA inputs.

| Sensor | Connect to: | Connection Location |
| --- | --- | --- |
| Tower Conductivity-Temperature | RED to S+, BLACK to S- WHITE to T+, GREEN to T- | Top circuit board, Part CT driver, Location A-B |
| pH | Clear coaxial center to 1+ Tinned coaxial shield to 1- Green solution ground to | Top circuit board, Part OP driver, Location C |
| ORP | Clear coaxial center to 2+ Tinned coaxial shield to 2- | Top circuit board, Part OP driver, Location D |
| Dual 4-20mA Input | Please see CI insert in the help section of this manual. | Top circuit board, Location E-F Part CI driver |
| B1 Conductivity | BLACK to S1, WHITE to S1 | Top circuit board, Location I Part B driver |
| B2 Conductivity | BLACK to S2, WHITE to S1 | Top circuit board, Location J Part B driver |
| Make-up Watermeter | RED to O, BLACK to | Top circuit board, Bottom, center terminals |
| Bleed Watermeter | RED to P, BLACK to | Top circuit board, Bottom, center terminals |
| Flowswitch | RED to T, RED to | Top circuit board, Bottom, center terminals |
| B1 Operating (Interlock) | BLACK to U, WHITE to | Top circuit board, Bottom, center terminals |
| B2 Operating (Interlock) | BLACK to V, WHITE to | Top circuit board, Bottom, center terminals |

Warning:

Do not route sensor, flowswitch and water meter cables in the same conduit as 120VAC power, pumps and solenoids.

Default Passwords

| User ID | Default Password | Note |
| --- | --- | --- |
| Admin | AAAA | Case sensitive |
| User No.1 | 1 | Default is Keypad passwords OFF |
| User No.2 | 2 | Browser passwords are always ON |
| User No.3 | 3 |  |
| User No.4 | 4 | Passwords may be changed |
| User No.5 | 5 | using Keypad OR Browser |
| User No.6 | 6 |  |
| User No.7 | 7 |  |

Typical Valve and Solenoid Wiring Color Coding

Terminate Green grounding cabling to bottom, center of aluminum backplate

Typical Valve and Sensor Locations

Captured Sample Blowdown Control

Automated blowdown control operates with Isolation Valves open,

Bypass Valve closed and Throttling Valve 15-25% open.

Optional Hardwiring

If you elect not to use the plug boxes or power plug provided with the controller.

Refer to the following table for hardwiring 120VAC.

Use multiple strand, AWG14 for 120VAC service, pumps and solenoid

| Service | Cable: | Connect to Lower circuit board | Notes: |
| --- | --- | --- | --- |
| Controller 120VAC 15Amp service | Line / Black Neutral / White Ground / Green | Center terminal block L N Aluminum backplate grounding screw. | Maximum controller 13.6 Amps @ 120VAC Existing flying lead grounds Controller to aluminum backplate. |
| Inhibitor Pump | Line / Black Neutral / White | Relays 1-3 NO1 Neutral | Relay No.1 |
| Bleed Solenoid | Line / Black Neutral / White | Relays 1-3 NO2 Neutral | Relay No.2 |
| Acid Pump | Line / Black Neutral / White | Relays 1-3 NO3 Neutral | Relay No.3 |
| Oxidant Pump | Line / Black Neutral / White | Relays 4-5 NO4 Neutral | Relay No.4 |
| Biocide Pump 1 | Line / Black Neutral / White | Relays 4-5 NO5 Neutral | Relay No.5 |
| Biocide Pump 2 | Line / Black Neutral / White | Relays 6-8 NO6 Neutral | Relay No.6 |
| Biocide Pump 3 | Line / Black Neutral / White | Relays 6-8 NO7 Neutral | Relay No.7 |
| Biocide Pump 4 | Line / Black Neutral / White | Relays 6-8 NO8 Neutral | Relay No.8 |
| B1 Blowdown Valve OR | NO / Black NC / Red Neutral / White | Relays 9-10 NO9 Relays 9-10 NC9 Neutral | Blowdown 1 controlled by Relay No.9 |
| B1 Blowdown Solenoid | Line / Red Neutral / Red | Relays 9-10 NO9 Neutral | Blowdown 1 controlled by Relay No.9 |
| B2 Blowdown Valve OR | NO / Black NC / Red Neutral / White | Relays 9-10 NO10 Relays 9-10 NC10 Neutral | Blowdown 2 controlled by Relay No.10 |
| B2 Blowdown Solenoid | Line / Red Neutral / Red | Relays 9-10 NO10 Neutral | Blowdown 2 controlled by Relay No.10 |